Product Specification

27 53 13 Wireless Clock System

Primex 72MHz OneVue™ Sync Wireless Clock System

Last update: 7/31/2026

Specifier Note: This product specification is written according to the Construction Specifications Institute (CSI), MasterFormatTM, SectionFormat, and PageFormat, contained in the CSI Manual of Practice. The section must be carefully reviewed and edited by the Architect/Engineer/Consultant to meet the requirements of the project and local building code. Coordinate this section with other specification sections and the drawings. Delete all “Specifier Notes” when editing this specification.

CONTENTS

27 53 13 Wireless Clock System	1

PART 1 GENERAL	3

1.1 GENERAL REQUIREMENTS & SCOPE	3

1.2 RELATED SECTIONS	3

1.3 REFERENCES	3

1.4 DEFINITIONS	3

1.5 SYSTEM DESCRIPTION	4

1.6 REGULATORY REQUIREMENTS	6

1.7 SUBMITTALS	6

1.8 SUBSTITUTIONS	7

1.9 QUALITY ASSURANCE	7

1.10 DELIVERY STORAGE AND HANDLING	7

1.11 PROJECT SITE CONDITIONS	7

1.12 SYSTEM STARTUP	8

1.13 WARRANTY	8

PART 2 PRODUCTS	9

2.1 SECTION INCLUDES	9

2.2 Manufacturer	9

2.3 SYSTEM OPERATION	9

2.4 EQUIPMENT	10

PART 3 EXECUTION	19

3.1 EXAMINATION	19

3.2 INSTALLATION	19

3.3 FIELD INSPECTION	21

3.4 MANUFACTURER SERVICES	21

3.5 CLEANING	22

3.6 DEMONSTRATION	22

3.7 PROTECTION	22

3.8 TESTING	22

PART 1 GENERAL

1.1 GENERAL REQUIREMENTS & SCOPE

The system is specified as described.

- Furnish and install a complete new Wireless Clock System using the Primex 72MHz OneVue™ Sync Wireless Clock System.

- Furnish and install all system equipment, devices, accessories, and material in accordance with these specifications and drawing to provide a complete and operating system.

- All bids shall be based on the equipment as specified herein. The model designations are that of Primex, Inc. The specifying authority must approve any alternate system

Specifier Note: Edit the following list as required for the project.

- System shall include the System Devices

Transmitter (master)

Repeater Transmitter (secondary)

GPS Receiver

Analog Clocks

Digital Clocks

Digital Elapsed Timers

Digital Code Blue Timers

1.2 RELATED SECTIONS

Specifier Note: Edit the following list as required for the project. List other sections with work directly related to this section.

- Division 26 “Electrical”

- Division 26 Section “Common Work Results for Electrical”

1.3 REFERENCES

System devices specified shall meet or exceed the requirements of the following.

Specifier Note: List standards referenced in this section, complete with designations and titles. This article does not require compliance with standards, but is merely a list of those used.

- National Fire Protection Association (NFPA): 1. NFPA 70 - National Electrical Code (NEC).

- Manufacturer Installation and User Guides and online help system.

1.4 DEFINITIONS

This section provides commonly used terms within this specification.

- GPS: Global Positioning System, a worldwide system that employs a constellation of satellites in an integrated network to determine geographic location anywhere in the world, and which employs and transmits Universal Coordinated Time, the world’s most accurate and reliable time.

- NTP: Network Time Protocol, used for synchronizing the clocks on computer networks and devices from either a public server or a separate server on a private local area network.

- UTC: Universal Coordinated Time

1.5 SYSTEM DESCRIPTION

Specifier Note: System description is based on the Primex Wireless Clock System.

- System shall operate on a 72MHz frequency. The 72MHz frequency efficiently transmits its signal through common building materials and across longer distances with less interference - ensuring all system devices receive system data updates.

- System transmitter shall require a FCC license for operation, resulting in a safe and interference free operation.

- Manufacturer shall offer system transmitters with a variety of power output levels to provide coverage for a single building or an entire campus.

- Manufacturer to provide design analysis to determine transmitter size and guaranteed signal coverage. Manufacturers that cannot provide this service shall not be considered.

- System shall wirelessly synchronize clocks and/or timers, and shall be capable of clock readouts in multiple time zones where desired.

- System shall provide a master time source that is transmitted wirelessly from the system master transmitter to secondary system devices. The master time source can either from a system supplied GPS Receiver or from an OWNER defined internal or external NTP server that the master transmitter can access via the OWNER'S Local Area Network (LAN). Up to three designated NTP Servers may be specified to ensure continuity of time synchronization. The master time will be synchronized to UTC.

- Hard wiring of system clocks for data communication shall not be required.

- System clocks shall automatically adjust for Daylight Saving Time in locations where DST is observed.

- Each system clock and other components shall use both precise time and synchronized time.

- Digital clocks shall be synchronized to within 10 milliseconds every 10 minutes and the system shall have an internal oscillator that maintains plus or minus four seconds per day between synchronization, so that clock accuracy shall not exceed plus or minus 0.2 seconds.

- Analog Clocks shall be synchronized to within 10 milliseconds 6 times per day when operating clock strikes 2:01 AM, 6:01 AM, 10:01 AM, 2:01 PM, 6:01 PM, and 10:01 PM, and the system shall have an internal oscillator that maintains plus or minus one second per day between synchronization, so that clock accuracy shall not exceed plus or minus 0.2 seconds.

- System shall include an internal clock reference so that failure to detect the master time source shall not result in the system clocks failing to indicate time. Additionally, system transmitters shall have an internal battery backup of up to eight hours in the event of a power failure so that settings and the correct master time will be instantly recalled upon restoration of power.

- System shall incorporate a “fail-safe” design so that failure of any component shall not cause failure of the system. Upon restoration of power or repair of failed component, the system shall resume normal operation without the need to reset the system or any component thereof.

- If a system transmitter stops transmitting valid time signals due to power failure, the system analog clocks will continue to function as accurate quartz clocks until a valid time signal is decoded. If signal transmission is not restored for three consecutive days, a clock's second hand will “two-step” as a visual indicator that the signal has been lost. A system digital clock/timer that has not decoded a valid time signal for a three consecutive days will display a visual indicator by flashing its colons continuously until a valid time signal is received. Should clocks lose both power and signal, the clocks will not function.

- Clock locations shall be as indicated and clocks shall be fully portable, capable of being relocated at any time.

- System shall provide a mobile configurator app (available for both iOS and Android) that allows OWNER to on-board a new transmitter and manage transmitter settings.

- System transmitters shall be equipped with Bluetooth® low energy wireless technology that allows the devices to send and receive communication to and from the system mobile configurator app.

- System shall include access to the Manufacturer system cloud-based software that allows OWNER to manage and monitor system transmitters and receive remote support services. Optionally, the system transmitters can be set to stand-alone mode, which does not allow for remote support services. A system that requires stand-alone computer-based system software or server hardware for system management or monitoring does not meet the requirements for this specification.

- System transmitters shall require connection to OWNER'S existing wired Ethernet network (DHCP or Non-DHCP) to use NTP as its time source and to also send data to and download settings from the system software.

- System software and mobile configurator app shall allow for over-the-air (OTA) firmware updates to a system transmitters.

- System software shall log, store, and display all operating diagnostic errors received from a system transmitter.

- U.S. only: System must operate in accordance with a “Radio Station Authorization”, Form FCC 601 – LM, granted by the Federal Communications Commission (FCC). This license will be issued to and held by the end user.

- CANADA only: The system must operate in accordance with a “Technical Acceptance Certificate” issued under the authority of Industry Canada and the Ministry of Industry. This license will be granted to and held by the end user.

System Software

Shall meet the below specifications:

- Software interface shall allow the OWNER'S system admin user(s) to manage the system components, including: system transmitter settings, reports, alert rules, system-wide user password complexity settings and user session timeout setting, manage system users and grant user access to system data and features.

- System software shall allow each system user to manage their own system profile, including their log in email address, password, alert notification preferences, and contact settings.

- System software shall be licensed and delivered via a Software-as-a-Service (SaaS) model and is built-on and powered by Amazon Web Services (AWS).

- System software shall include and provide all software and transmitter firmware revision updates.

- Shall not require the installation of on-site system hardware or software, with the exception of the system transmitter devices that transmit data to and download settings from the system software.

- Shall maintain and store redundant, data backups for up to seven years.

- Shall allow system users to access system software from a web browser on a mobile or tablet device or computer with an internet connection and does not require the installation of software or other third-party plug-ins or applications.

- Shall allow OWNER system admin user(s) to grant and control the data and features available to system users.

- Shall provide a dashboard view that displays the state of system transmitters and a list of system alerts and system notifications.

- Shall allow each system user to manage their own system profile, including their log in email address, password, alert notification preferences, and contact settings.

- Shall allow system users to view current and historical data transmitted by system transmitter devices and the settings of system components. The data and settings viewable to a user shall be limited to the role(s) assigned to their system user profile.

- Shall allow system users to enter comments to transmitter state-change events.

- Shall allow systems users to customize how data views are displayed within their system user account.

- Shall allow user-defined reporting; store and present system historical data in the form of system reports. User-defined data shall include the system transmitter devices included in a report, the frequency a report is system generated, and a specific range of data included in a report. System reports shall be displayed in the system software electronically within the interface and allow a system user to print and download reports. System shall also allow report data to be restricted based on the role(s) assigned to a system user.

- Shall generate alert notifications to system users 24 hours a day, 365 days a year by user's alert preference. User alert preferences option shall include to receive email, text, or voice notifications.

- Shall allow system users to acknowledge system alerts within the system software or from a voice alert notification. And system shall record and store the history of all alerting data and system user actions.

- All system user software access sessions between the web browser and the system software shall be encrypted by the HTTPS protocol.

- Network communication of the system transmitter to and from system software shall be secure and encrypted using the Transport Layer Security (TLS) encryption protocol and Secure Hypertext Transfer Protocol (HTTPS) authentication.

1.6 REGULATORY REQUIREMENTS

- Equipment and components furnished shall be of Manufacturer latest model.

- System shall be installed in compliance with local and state authorities having jurisdiction.

- U.S. only: The end user will hold a license, known as a “Radio Station Authorization” granted by the FCC. This license grants the end user protected use for wireless transmission at the designated frequency. This license will designate a unique “call sign” for each end user.

- U.S. only: Transmitter and receiver shall comply with Part 90 of FCC rules as follows: This device may not cause harmful interference. This device must accept interference received, including interference that may cause undesired operation. Transmitter frequency shall be governed by FCC Part 90.35. Transmitter output power shall be governed by FCC Part 90 257 (b).

- CANADA only: The end user will hold a license, known as a “Non Complex Fixed Station” Radio License granted by Industry Canada and the Ministry of Industry. This license grants the end user protected use for wireless transmission at the designated frequency.

- CANADA only: IC-2365: Application for “License to Install and Operate a Radio Station in Canada” must be completed and signed by end user prior to license issuance. The end user will grant permission for Primex to apply for the license on their behalf. Primex will provide all documents and technical information to Industry Canada for approval. This license will designate a unique “call sign” for each end user.

- CANADA only: Transmitter and receiver shall comply with RSS 119 of Issue 6 of Industry Canada specifications as follows: This device may not cause harmful interference, and this device must accept interference received, including interference that may cause undesired operation. Transmitter frequency shall be governed by IC: RSS119 Issue Transmitter output power shall be governed by IC: RSS119 Issue 6.

1.7 SUBMITTALS

- Product Data: Submit complete catalog data for each component, describing physical characteristics and method of installation. Submit brochure showing available colors, styles, sizes, and finishes of clocks.

- Samples: Submit one specified system device model(s) for approval. Approved sample(s) shall be tagged and shall be installed in the work at location directed.

- Manufacturer Instructions: Submit complete installation, set-up and maintenance instructions.

- Floor plans indicating the location of system transmitter(s), approved by Manufacturer, will be submitted to Owner prior to installation.

US Specifier Note: In accordance with FCC regulations, an application for “Radio Station Authorization” must be filed prior to use of the equipment. Normally, the Manufacturer will have completed the filing and obtaining the license. If not, the Owner will be required to file the application with the FCC prior to use. Furnishing the license, or a copy of the application, will confirm that FCC approval has been obtained. CANADA Specifier Note: In accordance with Industry Canada regulations, an application for “Technical Acceptance Certificate” must be filed prior to use of the equipment. Normally, the Manufacturer will have completed the filing and obtaining the license. If not, the Owner will be required to file the application with the Industry Canada prior to use. Furnishing the license, or a copy of the application, will confirm that Industry Canada approval has been obtained.

- U.S. only: Operating License: Submit evidence of application for FCC Radio Station Authorization prior to installing equipment. Furnish the license or a copy of the application for the license, to the Owner/End User prior to operating the equipment. The original license must be delivered to the Owner/End User.

- CANADA only: Submit IC Technical Acceptance Certificate prior to installing equipment. Furnish the license or a copy of the application for the license, to the Owner/End User prior to operating the equipment. The original license must be delivered to the Owner/End User.

1.8 SUBSTITUTIONS

- Proposed substitutions, to be considered, shall be manufactured of equivalent materials that meet or exceed specified requirements of this Section.

- Proposed substitutions shall be identified not less than 10 days prior to bid date.

- Other systems requiring wiring and/or conduit between master and clocks and/or timers will not be accepted.

- Other systems using wireless technology in an unlicensed frequency range will not be accepted.

- Other systems using wireless technology where the license is held by any party other than the end user will not be accepted.

1.9 QUALITY ASSURANCE

- U.S. only: Permits: Operating license for the transmitter from the FCC.

- CANADA only: IC-2365: Application for “License to Install and Operate a Radio Station in Canada” must be completed and signed by end user prior to license issuance.

- Qualifications Manufacturer: Company specializing in manufacturing commercial time system products with a minimum of 30 continuous years of documented experience including 10 or more years of experience producing GPS wireless time systems.

- Installer: Company with documented experience in the installation of commercial time systems.

- Prior to installation a site survey must be performed to determine proper transmitter placement.

1.10 DELIVERY STORAGE AND HANDLING

- Deliver all components to the site in the Manufacturer original packaging.

- Packaging shall contain Manufacturer name and address, product identification number, and other related information.

- Store equipment in finished building and in unopened packaging until ready for installation.

1.11 PROJECT SITE CONDITIONS

- Clocks and/or Timers shall not be installed until painting and other finish work in each room is complete.

- Mobile configurator app: installed on a mobile device meeting the app install requirements.

- Transmitter with an external antenna: Coordinate installation of system antenna for access to the roof to comply with safety standards detailed in Manufacturer instructions and per local codes.

- GPS Receiver time source: Coordinate installation of device for access to the roof or exterior side wall per Manufacturer installation instructions.

1.12 SYSTEM STARTUP

- At completion of installation and prior to final acceptance, turn on the equipment; ensure that all equipment is operating properly, and that all system devices and components are functioning.

1.13 WARRANTY

- Manufacturer shall provide a 5 year limited warranty on system transmitters, clocks, digital timers, timer control switch, and GPS Receiver.

- All other system components shall have a 1 year limited warranty, including external antennas and components and universal power supply (UPS).

PART 2 PRODUCTS

2.1 SECTION INCLUDES

- The system and equipment is specified as described in this section.

- All bids shall be based on the equipment as specified herein. The model designations are that of Primex. The specifying authority must approve an alternate system.

2.2 Manufacturer

- System shall be manufactured by:

Primex, Inc. 965 Wells St, Lake Geneva, WI 53147 | Phone: (855) 557-0337 | info@primexinc.com | www.primexinc.com

2.3 SYSTEM OPERATION

The system shall perform in the sequence of operation as described below.

- Install system transmitters and components, including internal or external antenna and optional GPS Receiver, detailed in Manufacturer installation instructions.

- Configure system transmitter settings through mobile configurator app detailed in Manufacturer instructions.

- Configure and install system clock devices per model specifications detailed in Manufacturer installation instructions.

Master transmitter operation

Specifier Note: Select the system’s specified master time source:

- When power is first applied, it looks for a master time source (first GPS and then NTP). If a master time source is not found, it uses its onboard real time clock (RTC) and continues to search for its master time source. If time source is not found, transmitter is set to a warning state with a time sync failure status, its caution LED status indicator is illuminated, and transmits its state to the system software at its scheduled check-in time (default set to every 5 minutes). If it fails to get time from either source consecutively for 30 minutes (default), it enters an alarm state and its error LED indicator is illuminated. If the RTC clock is off significantly, the transmitter will report a critical error to OneVue. This will occur only after the first 30 minutes of operation if the RTC continues to be significantly off.

- GPS Time Source: With the transmitter in GPS mode, it powers to a connected GPS receiver mounted with a clear view of the sky. Upon power, the GPS receiver seeks the GPS satellites in orbit to determine position and UTC time. Once the transmitter acknowledges receivable GPS data, it downloads time data and synchronizes its internal master clock to GPS time. The transmitter then starts to transmit its internal time once every second. The transmitter updates its internal clock every time it receives valid time data from the GPS.

- NTP Time Source: Transmitter connects over the OWNER'S Ethernet to the IP address of the NTP server. This IP address is programmed into the transmitter as part of its setting configuration. Once the connection to the NTP server is acknowledged, it downloads time data and synchronizes its internal master clock to received NTP time. The transmitter then starts to transmit its internal time once every second. The transmitter updates its internal clock in this mode once every 5 minutes by system default (end-user setting). Transmitter configuration allows up to three NTP servers for fail-over purposes.

Clock operation

- After initial setup, the clock and/or timer shuts off its receiver. Six times each day an analog clock microprocessor activates its receiver and starting with the stored channel it search for a valid time signal. Every 10 minutes a digital clock/timer activates its receiver and starting with the stored channel search for a valid time signal. If necessary, the clocks will resynchronize to the correct time.

- If an analog clock has not decoded a valid time signal for three consecutive days, it enters step mode. Low battery voltage is a common cause of the clock to not properly decode a time signal. If a clock goes into step mode, replace its batteries first and then determine if the clock synchronizes to master time source before attempting other troubleshooting methods.

- If a digital clock/timer has not decoded a valid time signal for three consecutive days, its display colon indicator flashes continuously until a valid time signal is received.

2.4 EQUIPMENT

The system shall include all equipment as specified.

Specifier Note: Only include transmitter models specified.

Supply following transmitter model(s)

- 1 Watt Transmitter with internal antenna, Ethernet Port (with GPS)

- 1 Watt Transmitter with external antenna, NTP and GPS Input

- 1 Watt Transmitter with internal antenna, NTP or Repeater capability

- 5 Watt Transmitter with external antenna, NTP and GPS input

- 30 Watt Transmitter with external antenna, NTP and GPS input

Specifier Note: Exclude external antenna section below if Transmitter(s) with an internal antenna is specified.

Supply following external antenna

- Non-penetrating Mast Antenna Kit

- Pipe to Pipe Mast Antenna Kit (for use with 5 and 30 Watt Tansmitters)

- Non-penetrating Mast Antenna Kit

Transmitter general specifications

- User-defined settings (mobile app): Time Zone, Daylight Saving Time bypass option, up to three NTP time sources, Power-on Transmit Schedule, Normal Transmit Schedule, Firmware, and Repeater Channel for a secondary (repeater) transmitter.

- User-defined settings (system software): Legacy Clock Time Zone, Alarm Delay, Firmware, Unresponsive Timeout, and Check-in Interval.

- Front panel: four LED status indicators (Power, Transmit, Caution, Error) and Bluetooth labeled push-button to pair transmitter with the system mobile configurator app.

- Rear panel: Network LAN port (RJ-45 Ethernet, 100/10 Mbps, 802.3 Ethernet), GPS In port (MiniDIN 7-Pin), External Antenna connector (coaxial, n-male), Baseboard Monitor port (MiniDIN 9-Pin, for use with 5 or 30 Watt Transmitter only), dry contact closure relay panel (for use with specified Primex products), and pin port to allow end-user connection initiation (check-in) to system software.

- Equipped with Bluetooth® low energy (v5) wireless technology to allow pairing with system mobile configurator app for setting management.

- An onboard real time clock (RTC) such that failure to receive time from master time source will not disable the operation of the system clocks.

- Time zone adjustment for all time zones in the world and includes Eastern, Central, Mountain, Pacific, Alaska, and Hawaii.

- Manufacturer or authorized certified installer shall configure the transmitter FCC call sign and RF channel number. These settings are to be predetermined during the FCC licensing process based on system installation location and existing wireless services operating in the area. The OWNER will be required to contact Manufacturer or authorized certified installer if, for any reason, a different broadcast channel is required, since the request would require a modification of the license, requiring approval by the US: FCC or CANADA: by Industry Canada. The system OWNER is the sole proprietor of the FCC License and manufacturer or certified installer are acting as agents. Changes to channel or other FCC regulated configuration settings following the installation by the manufacturer or certified installer are the sole responsibility of the OWNER, and should only be done in accordance with FCC regulations.

1 Watt Transmitter specifications

Transmitter shall meet the specifications below:

- 1-Watt maximum transmission (at transmitter)

- 72MHz frequency range

- 49 channels available (pre-programmed prior to shipment)

- Dimensions: 17.0”L x 12.0”W x 1.7”D (43.2cm x 30.5cm x 4.32cm)

- Weight: 9 lb.. (4 kg)

- Power Supply: Input: 120 VAC, 50/60 Hz, 0.6 Amp | Output: 9 VDC, 2.78 Amp, 6 ft. (1.8 m) cord

- Operating Range: 32° to 122°F (0° to 50°C)

Internal antenna specifications (1 Watt Transmitter)

Transmitter shall include an internal antenna that is fastened to the top of the unit.

- Antenna: 46.0 in. L (116.8 cm)

- Weight: 7.75 lb. (3.5k g)

5 and 30 Watt Transmitter specifications

Transmitter shall meet the specifications below.

- Operating Frequency Range: 72MHz

- Enclosure Dimensions: 22”W x 17”H x 22”D (55.88cm x 43.18cm 55.88cm)

- Approx. Weight: 55 lb. (24.9 kg)

- Power Supply: 120 VAC, 50/60 Hz, 6.0A Max

- Oversized heat sink provides adequate cooling

- Amplifier Output Bandwidth: >20 MHz maximum

External antenna specifications

Specifier Note: Section only applies to EXTERNAL Antenna Transmitter models. Delete if a 1 Watt Transmitter with an Internal Antenna Transmitter model is specified.

Transmitter shall include an external antenna that meets the below specifications

- Antenna connects to the transmitter via a 100 ft. (30.5m) 50-ohm coaxial cable.

- 5 and 30 Watt models: External Antenna must be installed by Primex or a certified Primex installer.

- Cabling: Maximum 100 ft. (30.48 m) between transmitter and antenna

- FCC Part 90 Accepted

- IC RSS-119 Accepted

- Weight: 9 lb. (4.1 kg)

- Shall include an Outdoor Ground Plane Antenna that meets the specification below:

Dimensions: 29.4”H x 41.5”W (74.7cm x 105.41cm)

Lightning Protection: Direct Ground

Cabling: 100 ft. (30.48 m) between transmitter and antenna provided

FCC Part 90 Accepted

IC RSS-119 Accepted

Weight: 8.25 lb. (3.75 kg)

GPS Receiver specifications

Specifier Note: If using NTP only for time source input, you may delete this section.

- External Antenna model: GPS roof mounted with 16 ft. (5 m) cable attached. GPS Receiver shall be a complete GPS receiver including antenna in a waterproof case, designed for roof or outdoor mounting. Provide mounting bracket for attachment to roof structure.

- Internal Antenna model: GPS roof mounted, with 10 ft. cable (3 m) attached.

- An GPS extension cable is available from the Manufacturer, 50 ft. (15.25 m), 100 ft. (30.5 m), or 200 ft. (61 m). Use with an external antenna: total GPS cable length cannot exceed 100 ft. (30.5 m).

- GPS Receiver cable must be plenum rated where required by local code.

- GPS connection to main Transmitter requires ferrite bead connector (supplied with transmitter).

Repeater Transmitter

Specifier Note: Large buildings and multi-building projects may require repeater transmitter to provide proper coverage. Consult Primex for assistance in making this determination. If repeater transmitters are required, include this section.

- Shall receive signal from master Transmitter and transmit the signal to the system devices in its vicinity, which are out of range from the master transmitter.

Analog Clocks

Clocks shall meet the following specifications:

- Analog clocks shall be wall mounted.

- Face shall be white. Hour and minute hands shall be black.

- Additional colors, finishes, and dial faces are available from Manufacturer.

- Clock faces can be customized by Manufacturer to display organization name or logo as specified.

- Clock frames and lenses are of durable thermoplastic.

- Clocks shall have a tamper proof/theft resistant clock-lock mounting slots.

- Analog clocks shall be capable of automatically adjusting for Daylight Saving Time. An on-off switch located on the transmitter shall disable this function if desired.

- Clock shall have either a battery-power or a 120 VAC power supply built into the clock assembly.

- If power is interrupted, the clock will stop until power resumes. Upon resumption of power, the clock will self correct to the current time.

- Electric (AC) models will include a two prong plug. The power cord can be cut to length and sliced as needed for hard wired installation.

- Battery-operated analog clocks shall have up to a 5-year battery life. Battery life is based on common operating conditions and may very due to installed site conditions.

- Installer will furnish clock batteries in accordance with Manufacturer instructions.

- Time shall be automatically updated from the transmitter 6 times per day.

- If the transmitter stops transmitting valid time signals due to power failure, the clocks will continue to function as accurate quartz clocks until a valid time signal is decoded. If signal transmission is not restored after 96 hours, the second hand will “two -step” as a visual indicator that the signal has been lost. Should the clocks lose both power and signal, the clocks will not function.

- Analog clock receivers shall be as follows: Receiver sensitivity: >-110 dBm, Receiver power: Dual Alkaline batteries or AC-powered, Antenna type: internal, Antenna gain: -7 dBd

- SUPPLY MODELS - Traditional Series Analog Clocks

(Power Source) Description

(Battery) 9” (22.86cm) Black

(Battery) 12.5” (31.75cm) Black

(Battery) 12.5" (31.75cm) White

Battery) 16" (40.64cm) Black

(Electric) 12.5” (31.75cm) 120VAC Black

(Electric) 12.5” (31.75cm) 120VAC White

(Electric) 16” (40.64cm) 120VAC Black

(Battery) 12.5” (31.75cm) Black, Remote Antenna Clock

(Battery) 12.5” (31.75cm) White, Remote Antenna Clock

- SUPPLY MODELS - Slim Series Analog Clocks

Slim Metal Series Clock

(Power Source) Description

(Battery) 12.5" (31.8cm) Slim Mode

(Electric) 12.5" (31.8cm) Slim Mode

(Battery) 16” (40.6cm) Slim Model

(Electric) 16” (40.6cm) Slim Model

- SUPPLY MODELS - Gallery Series Analog Clocks

Analog Gallery Series

(Power Source) Description

(Battery) 24” (61cm) Distressed Brown Gallery Series Clock Roman Dial

(Battery) 24” (61cm) Distressed Brown Gallery Series Clock Arabic Dial

(Electric) 24” (61cm) Distressed Brown Gallery Series Clock Roman Dial

(Electric) 24” (61cm) Distressed Brown Gallery Series Clock Arabic Dial

- SUPPLY MODELS - Wood Series Analog Clocks

Wood Series Analog Clocks

Battery-Powered Clocks

Description

11.5” (29.21cm) Honey Arabic

11.5” (29.21cm) Honey Roman

11.5” (29.21cm) Dark Cherry Arabic

11.5” (29.21cm) Dark Cherry Roman

11.5” (29.21cm) Clear Oak Arabic

11.5” (29.21cm) Clear Oak Roman

11.5” (29.21cm) Walnut Arabic

11.5” (29.21cm) Walnut Roman

16” (40.64cm) Clear Oak Arabic

16” (40.6cm) Clear Oak Roman

16” (40.64cm) Dark Cherry Arabic

16” (40.6cm) Dark Cherry Roman

16” (40.6cm) Honey Roman

16” (40.6cm) Honey Arabic

16” (40.6cm) Walnut Roman

16” (40.6cm) Walnut Arabic

AC-Powered Clocks

Description

16” (40.64cm) Honey Arabic

16” (40.64cm) Honey Roman

16” (40.64cm) Dark Cherry Arabic

16” (40.64cm) Dark Cherry Roman

16” (40.64cm) Clear Oak Arabic

16” (40.64cm) Clear Oak Roman

16” (40.64cm) Walnut Arabic

16” (40.64cm) Walnut Roman

Digital Clocks

Clocks shall meet the following specifications.

- Digital Clock must be able to receive synchronized time signal from the master or satellite transmitter.

- Digital Clock display must include a 12 or 24-hour time display, a PM indicator light, and an alternating time and date display option.

- Surface-mount models are available from the Manufacturer.

- Flush-mount models are available from the Manufacturer.

- Dual-mount models are available from the Manufacturer; dual mount kit.

- Digital Clock shall be capable of automatically adjusting for Daylight Saving Time.

- Digital Clock shall have either a 120 VAC or 24 VAC power supply built into the clock assembly.

- 120 VAC Digital Timer will include a power cord with a two prong plug. Power cord can be trimmed to length and spliced as needed for hard wired installation.

- 24 VAC Digital timer will include a power cord with pigtail to be hard wired to building 24VAC power grid.

- Digital Clock must be viewable from 150 ft. (45.7 m).

- Digital Clock must have highly visible 7-segment LED digits.

- Digital Clock shall have three display dimmer options, 75%, 50%, and 25%.

- Digital Clock LED colors, sizes, digit layouts, and mount options are available from the Manufacturer.

- SUPPLY MODELS - Digital Clocks

Digital Clocks (Levo Series)

Surface-Mount with 2.5" Digits

Specifier Note: Indicate if 4-Digit or 6-Digit Model

Description

120VAC, 4° Slope Bracket, 10’ (3.0m) cord with plug

120VAC, 18° Slope Bracket, 10’ (3.0m) cord with plug

24VAC, 4° Slope Bracket, 12” (30.48cm) cord with pigtail

24VAC, 18° Slope Bracket, 12” (30.48cm) cord with pigtail

Surface Mount with 4" Digits

Specifier Note: Indicate if 4-Digit or 6-Digit Model

Description

120VAC, 4° Slope Bracket, 10’ (3.0m) cord with plug

24VAC, 4° Slope Bracket, 12” (30.48cm) cord with pigtail

Elapsed Timer

Timers shall meet the following specifications.

- Timer must also function as a clock or function as a count-down/count-up interval timer when programmed with a three button wall mount control switch.

- Timer must accurately count up or count down up to a maximum of 99 hours, 59 minutes, and 59 seconds.

- Timer shall include a three button wall mountable control switch. This control will be mounted in a single gang electrical box. Control cover plate shall be stainless steel. Control buttons must be washable with water and common disinfectants.

- Switch control shall connect to timer with a supplied reversed wire (cross-pinned) CAT5 cable with an RJ-45 connector or a reversed wire (cross-pinned) telephone cable with an RJ-11 connector. It can be extended up to 100 ft. (30.48 m).

- Timer switch control can be configured to simultaneously activate two connected timers.

- Timer shall be capable of automatically adjusting for Daylight Saving Time

- Timer must be viewable from 150 ft. (45.7 m).

- Timer must have highly visible 7-segment LED digits.

- Time shall have three display dimmer options, 75%, 50%, and 25%.

- Timer display shall include a 12 or 24-hour time display option, a PM indicator light, and an alternating time and date display option.

- Additional LED colors, sizes, digit layouts, mounts, and timer options are available from the Manufacturer.

- Timer must have an audible tone option on the count-up and count-time function with a frequency of 3KHz +/-0.5KHz.

- Timer shall have either a 120 VAC or 24 VAC power supply built into the clock assembly.

- SUPPLY MODELS - Elapsed Timers

Elapsed Timers

Surface-Mount Timers with 2.5" Digits

Description

120VAC, 4° Slope bracket, 10' (3.0m) cord with plug

24VAC, 4° Slope bracket, 12" (30.48cm) cord with pigtail

Flush-Mount Timer with 2.5" Digits

Description

120VAC, 30” (76cm) cord with pigtail

24 VAC, 12" (30.48cm) cord with pigtail

Surface-Mount Timers with 4" Digits

Description

120VAC, 4° Slope bracket, 10' (3.0m) cord with plug

24VAC, 4° Slope bracket, 12" (30.48cm) cord with pigtail

Code Blue Timer

Timers shall meet the following specifications.

- Timer must function as a clock and must integrate to OWNER'S existing code blue control system.

- Timer shall include a three button wall mountable control switch. The control switch will be mounted in a single gang electrical box.

- The timer switch control buttons must be washable with water and common disinfectants.

- The timer switch control shall connect to timer with a supplied reversed wire (cross-pinned) CAT5 cable with a RJ45 connector or a reversed wire (cross-pinned) telephone cable with an RJ-11 connector. It can be extended up to 100 ft. (30.48 m).

- Timer switch control can be configured to simultaneously activate two connected timers.

- Timer display must include a 12 or 24-hour time display, a PM indicator light, and an alternating time and date display option.

- Timer shall be capable of automatically adjusting for Daylight Saving Time.

- Timer must include an optional audible tone to alert changes in interval cycles in the count-up and count-down function.

- Timer must have adjustable brightness control.

- Timer must have power outage memory backup and maintain correct time for 8 hours without power.

- Timer shall have either a 120 VAC or 24 VAC power supply built into the clock assembly.

- SUPPLY MODELS - Code Blue Timer

Code Blue Timer - Levo Series

Timers with 2.5" Digits - 6-Digit

Description

120VAC, 4° Slope Bracket, 10’ (3.0m) cord with plug

120VAC, 18° Slope Bracket, 10’ (3.0m) cord with plug

24VAC, 4° Slope Bracket, 12" (30.48cm) cord with pigtail

24VAC, 18° Slope Bracket, 12" (30.48cm) cord with pigtail

Flush-Mount Timers with 2.5" Digits - 6-Digit

Description

120VAC, 30” (76cm) cord with pigtail

24 VAC, 12” (30.48cm) cord with pigtail

Timers with 4" Digits - 6-Digit

Description

120VAC, 4° Slope Bracket, 10’ (3.0m) cord with plug

24VAC, 4° Slope Bracket, 12" (30.48cm) cord with pigtail

Accessories

- System shall include the accessories below:

Analog Clock - Dual Clock Kit

Description

Black - Fits 12.5" Traditional Series or Educational Series Analog Clock

White - Fits 12.5" Traditional Series or Educational Series Analog Clock

Slim Metal Series Clock - Dual Clock Kit

Description

Fits 12.5” (31.75cm) Slim Model Clock

Fits 16” (40.6cm) Slim Model Clock

Digital Clock - Dual Clock Bracket Kit

Ceiling mount: [2", 4-Digit] [2", 6-Digit] [4", 4-Digit] [4", 6-Digit]

Wall mount: [2", 4-Digit ] [2", 6-Digit] [4", 4-Digit]

Digital Clock Polycarbonate Clock Guards

Description

2.5" (6.35cm) Guard: 16.0" L x 7.0" H x 5.5"D (40.64cm L x 17.78cm H x 13.97 cm D)

4" (10.16cm) Guard: 25.0" L x 9.8" H x 4.4" D (63.5cm L x 24.9cm H x 11.2 cm D)

Analog Clock Wire Clock Guard

Description

16" Clocks (40.64cm): 18" square x 3"D (45.72cm square x 7.6cm D)

Crash Cart Kit

Description

Complete kit for mounting a Digital Clock Timer to a mobile crash cart

Specifier Note: Where desired for mounting transmitter, specify the following "transmitter rack" (one for each transmitter).

1-Watt Transmitter Rack

  - 18 GA metal

  - Epoxy coated

  - 18”L x 3“H x 16.5“D (45.7cmL x 7.6cmH x 41.9cmD)

Description

1-Watt Transmitter Rack

Transmitter accessory pack - transmitter Rack and UPS

PART 3 EXECUTION

3.1 EXAMINATION

- Examine conditions with the Installer present for compliance with requirements and other conditions affecting the performance of the system and the system devices.

- Do not proceed until unsatisfactory conditions have been corrected.

- Verify that construction is complete in spaces to receive equipment and that rooms are clean and dry.

- Verify that 120 VAC electrical outlet is located within 5 ft. (1.5 m) of device and the outlet is operational and properly grounded.

- Timer Switch Control: Verify single gang electrical box for switch control is mounted and within 15 ft. (4.5 m) of digital display device. Verify pathway for connecting cable is available and compliant to local building codes.

- PoE devices: Verify that an active PoE port is located within close proximity to device.

3.2 INSTALLATION

Specifier Note: To assure optimum performance of the system, a site survey is recommended to be performed by Primex or a certified Primex Channel Partner. To assure optimum performance of the system, transmitter(s) location(s) must be specified in the construction documents.

- General: Install system devices in accordance with applicable codes.

- Install system devices in accordance with Manufacturer written instructions.

- Provide all system equipment necessary for a complete and operable system.

- Comply with requirements of Division 27 Sections "Common Work Results for Communications" and "Communications Horizontal Cabling."

- Cables: Install cables in raceways and cable trays except within consoles, cabinets, and desks [and except in accessible ceiling spaces and framed partitions where exposed wiring is allowed by Owner]. Install plenum cable where required. Conceal cable installation where possible.

Specifier Note: Valid for transmitter with GPS input. The GPS unit can be mounted on the roof, on a pole, or at a window. In each case, the GPS unit must have a clear view of the sky. If the GPS unit is mounted on the roof, it must be located on a suitable bracket, well above the level of standing or incidental water. If the GPS unit is mounted at a window, it must be located away from low-E glass. If transmitter to use NTP as time source, delete following work instruction with this note.

GPS Unit (INTERNAL Antenna Transmitter Model only):

- Install GPS unit on roof in location indicated, in clear view of the sky.

- Install unit in location free from standing water and above accumulations of leaves or debris.

- Seal cable connection to GPS with cable connection sealant.

- Any added cable lengths must be protected from outside elements.

GPS Unit (EXTERNAL Antenna Transmitter Model only):

- Locate transmitter in a penthouse, electrical closet or telecommunications room in a central location in the building.

- Clearance around all side of the transmitter to comply with local building codes.

Specifier Note: Select procedure appropriate to the master time source from either of the following:

If GPS Unit will be used as master time source:

- Attach GPS receiver cable to transmitter back panel.

- Set GPS/LAN DIP switch to GPS.

If NTP will be used as master time source:

Specifier Note: If NTP is the master time source, the network drop used to connect the transmitter must have connectivity to the NTP server, which can be verified by the owner's Information Technology department. The default NTP address is time.nist.gov. If the network has a different NTP IP address, it may be programmed into the transmitter by the installer to allow connection to the proper network time.

- Connect CAT5/CAT5e/CAT6 EIA/TIA standard Ethernet cable from transmitter back panel LAN port to available network drop.

Transmitter (EXTERNAL Antenna only)

- Transmitter is connected to external antenna via a 50 ohm coaxial cable. Typical length is 100 ft. (30.5 m)

- Cable routing should comply with ANSI EIA/TIA-569 and local building codes.

- If cable is routed through conduit, the conduit should be a minimum of 2 in. (50.8 mm) diameter.

- Transmitter enclosure must be bonded to an earth ground per ANSI EIA/TIA 607, NEC Article 250, and local building codes.

- Antenna should be mounted to a mast on the roof of the building connecting to the transmitter via a 50-ohm coaxial cable.

- Consult manufacturer instruction manual for specific clearances and mounting instructions.

- Antenna must be bonded to an earth ground per ANSI EIA/TIA 607, NEC Article 250, and local building codes.

Transmitter (INTERNAL Antenna only)

- Locate transmitter where indicated, a minimum of 2 to 3 ft. (.6 to 1 m) above the floor, away from large metal objects such as filing cabinets, lockers or metal framed walls.

- Transmitter(s) will be placed at locations indicated within specifications and drawings.

- Connect antenna to transmitter, using care not to strip threads.

- Connect power supply to the transmitter.

- Plug power supply into electrical outlet.

Analog Clocks

- Furnish all equipment necessary for a complete and operational system.

- Perform the following operations with each clock:

- Configure and set clock to correct time in accordance with manufacturer instructions.

- Observe clock until valid signals are received and clock adjusts itself to correct time.

- Install each clock per its model mounting specifications per manufacturer instructions and mounting instructions at the indicated location

Digital Clocks

- Cable routing must comply with ANSI EIA/TIA- 569-A and local building codes.

- Furnish all equipment necessary for a complete and operational system.

- Perform the following operations with each clock:

- Configure and set clock to correct time in accordance with manufacturer instructions.

- Observe clock until valid signals are received and clock adjusts itself to correct time.

- Install each clock per its model mounting specifications per manufacturer instructions and mounting instructions at the indicated location.

Digital Timers

- Cable routing must comply with ANSI EIA/TIA- 569-A and local building codes.

- Furnish all equipment necessary for a complete and operational system.

- Perform the following operations with each clock:

- Mount timer per model mounting specifications.

- Apply power per timer model power specifications.

- Connect timer to switch control unit with manufacturer provided cable or approved extension cable.

- Fasten timer to mounting bracket.

- Set time zone, time date option, and brightness level in accordance with manufacturer instructions and per owner requirements.

- Observe timer until valid time signal is received and timer displays correct time.

3.3 FIELD INSPECTION

- Inspection: Make observations to verify that system devices and components are properly labeled.

- Prior to final acceptance, inspect each system device and component, adjust as required, and replace parts which are found defective.

- At completion of system device installation and prior to final acceptance, turn on the equipment; ensure that all equipment is operating properly, and that the system and all system devices and components are functioning.

3.4 MANUFACTURER SERVICES

- System software and device manuals shall be assessable through Manufacturer online knowledge base

- Provide Manufacturer system commissioning in accordance with Manufacturer written recommendations. Perform operational testing to verify compliance with requirements. Adjust as required.

- Manufacturer to provide a specified level of system commissioning services.

Specifier Note: Only include one level of commissioning. Contact Primex for additional information.

- Phone commissioning: system deployment training, including system set up, validation of device configuration, and system functionality by way of a remote web conference.

- On-site commissioning: system deployment training, including system set up, validation of device configuration, system functionality, verification of device network connections, and device install training.

- Installation and full on-site commissioning: system training, software configuration, validation of device configuration, training on system functionality, verification of network use, device install training, and device installation.

3.5 CLEANING

- Prior to final acceptance, clean exposed surfaces of devices, using cleaning methods recommended by Manufacturer.

- Remove temporary labels from clock faces. Do not remove labels from backs of clocks.

3.6 DEMONSTRATION

- Provide training to OWNER'S representative on setting, adjusting and configuring device and routine maintenance.

- Provide training to OWNER'S representative on how to install or access the system provided software, adjusting and programming the transmitter, setting and adjusting system devices and routine maintenance

3.7 PROTECTION

- Protect finished installation until final acceptance of the project.

3.8 TESTING

- All devices must be tested at their operational location under normal operational conditions to ensure reception of signal.