Product Specification

27 52 33 - Environmental Conditions Monitoring System

OneVue™ Environmental Monitoring

Temperature, Temp and Humidity, and Differential Pressure Monitoring

Last update: 11/3/2021

Specifier Note: This product specification is written according to the Construction Specifications Institute (CSI), MasterFormatTM, SectionFormat, and PageFormat, contained in the CSI Manual of Practice. The section must be carefully reviewed and edited by the Architect/Engineer/Consultant to meet the requirements of the project and local building code. Coordinate this section with other specification sections and the drawings. Delete all “Specifier Notes” when editing this specification.

CONTENTS

27 52 33 - Environmental Conditions Monitoring System	1

PART 1 GENERAL	4

1.1 GENERAL REQUIREMENTS & SCOPE	4

1.2 RELATED SECTIONS	4

1.3 REFERENCES	4

1.4 DEFINITIONS	5

1.5 SYSTEM DESCRIPTION	5

1.6 REGULATORY REQUIREMENTS	8

1.7 SUBMITTALS	8

1.8 SUBSTITUTIONS	9

1.9 QUALITY ASSURANCE	9

1.10 DELIVERY STORAGE AND HANDLING	9

1.11 PROJECT SITE CONDITIONS	9

1.12 WARRANTY	9

1.13 SOFTWARE MAINTENANCE	9

PART 2 PRODUCTS	10

2.1 SECTION INCLUDES	10

2.2 MANUFACTURER	10

2.3 SYSTEM SOFTWARE	10

2.3 SYSTEM DEVICES & ACCESSORIES	11

PART 3 EXECUTION	16

3.1 EXAMINATION	16

3.2 INSTALLATION	16

3.3 FIELD INSPECTION	16

3.4 SERVICES	16

3.5 CLEANING	17

3.6 DEMONSTRATION	17

3.7 PROTECTION	17

3.8 TESTING	17

PART 1 GENERAL

1.1 GENERAL REQUIREMENTS & SCOPE

The system is specified as described.

- Furnish and install a complete new Environmental Monitoring System using the Primex Environmental Monitoring cloud-based platform that is built on the secure Amazon Web Services (AWS) infrastructure.

- Furnish and install all system devices, accessories, and material in accordance with these specifications and drawing to provide a complete and operating system.

- All bids shall be based on the equipment as specified herein. The model designations are that of Primex, Inc. The specifying authority must approve any alternate system

Specifier Note: Edit the following system devices as required for the project.

- System shall include the System Devices

Temperature and Humidity Sensors

Temperature Sensors

Temperature Sensor Probes

Temperature Sensor Thermobuffers

Differential Pressure Sensor

Device Accessories

1.2 RELATED SECTIONS

Specifier Note: Edit the following list as required for the project. List other sections with work directly related to this section.

- Division 26 “Electrical”

- Division 26 Section “Common Work Results for Electrical”

- Division 27 Section "Common Work Results for Communications"

- Division 27 Section "Communications Horizontal Cabling"

1.3 REFERENCES

System devices specified shall meet or exceed the requirements of the following.

Specifier Note: List standards referenced in this section, complete with designations and titles. This article does not require compliance with standards, but is merely a list of those used.

- National Fire Protection Association (NFPA): 1. NFPA 70 - National Electrical Code (NEC).

- FDA registered, 21 CFR Part 11 compliant

- FCC, CE, and IC compliant

- Manufacturer Installation and User Guides.

1.4 DEFINITIONS

This section provides commonly used terms within this specification.

- SaaS: Software-as-a-Service

- AWS: Amazon Web Services

- TLS: Transport Layer Security

- HTTPS: Hypertext Transfer Protocol Secure

- SMA: Software Maintenance Agreement

1.5 SYSTEM DESCRIPTION

Specifier Note: System description is based on the Primex OneVue™ Environmental Monitoring and Primex Sensor devices.

General Specifications

- System shall be licensed and delivered via a Software-as-a-Service (SaaS) model and is built-on and powered by Amazon Web Services (AWS).

- System is licensed on a subscription basis centrally hosted by Manufacturer and delivered to Owner as a cloud-based software system with system devices.

- Manufacturer shall offer subscription pricing models, which are to be inclusive of software access, technical support, enhancements, and maintenance.

- System shall not require the installation of on-site system hardware or software, with the exception of the system devices that transmit data to the system software.

- System shall maintain and store redundant, data backups.

- System can be scaled from a single building to a network of buildings, or an enterprise spread across many time zones.

- System software revisions and system device firmware revisions are provided under the Manufacturer subscription agreement.

- System devices shall transmit data to the system software over the Owner’s existing wireless or wired network.

- System software shall be accessed from a web browser and does not require the installation of software or other third-party plug-ins or applications.

- System users shall be able to access the system software from a web browser on a mobile or tablet device or computer with an internet connection.

- System shall provide automated monitoring, system data storage, alerting, and reporting of the system devices, and user-defined system software component settings.

- The system software shall provide a dashboard view that displays the state of all monitored assets and a list of system alerts and notifications.

- System software shall allow the Owner's system admin(s) to grant and control the data and features available to system users.

- System software shall allow system users to view current and historical data transmitted by system devices and the settings of system components. The data and settings viewable to a user shall be limited to the role(s) assigned to their system user profile, which is managed by Owner's system admin users.

- System software shall allow system users to enter comments to state-change events. The comments and event details are viewable from the system and are included in a system report.

- System software shall allow systems users to customize how data views are displayed within their system user account.

- System software shall allow system admin user to set system wide user password complexity settings and session timeout settings.

- System software shall have the ability to generate alert messages to system users 24 hours a day, 365 days a year.

- System software shall allow system alerts to be acknowledged by system users within the system software or from a voice alert message.

- The system shall record and store the history of all alerting data and user actions.

Encryption and Authentication

- All user sessions between the web browser and the system software shall be encrypted by the HTTPS protocol.

- All system device communication over the Owner's network shall be secure and encrypted using the Transport Layer Security (TLS) encryption protocol and Secure Hypertext Transfer Protocol (HTTPS) authentication.

System Administration

Software interface shall allow the Owner's system admin user(s) to manage the system components, including:

Manage system device settings. Create and manage alert rules to notify staff when a condition may warrant corrective action or maintenance. Create and manage teams to allow the appropriate staff to be notified of alerting conditions based on staffing schedules. Create and manage reports to allow system users to view and download current and historical system data. Set system-wide password complexity settings and session timeout setting to align with Owner information security policies and procedures. Create system users and grant user access to system data and features, activate and deactivate system users, and view user log in history.

The Owner's system admin user(s) shall have the ability to create, edit, and delete system alert rules and settings, including:

Create staff shift schedules and associate shift schedules to alert rules. Specify the system devices assigned to an alert rule. Specify the conditions that generate alerts to system users. Specify the system users that receive alert notifications. Specify the frequency alert notification are generated during an alerting condition. Specify staff that are to receive an escalation alert message and when an escalation alert message is sent.

The system shall allow each system user to manage their own system profile, including.

Specifying the method(s) of preference in which they receive alert messages. Managing their user profile email address, password, and contact settings.

The system shall allow system device settings to be user-defined within the system software to meet Owner requirements, including:

Low and High Range (expected normal operating range). Set the unit of measurement for device readings. Set the frequency readings are logged and transmitted to system. Set the maximum amount of time a system device can go without transmitting its data to the system. Set if the system device audio alert is enabled or disabled and set audio alert resume time period. Assign a primary and alternate network used by system devices to connect to Owner's network to transmit data to system and download settings managed from the system. Migrate devices from one network to another without an interruption of network connection. Assign a static IPv4 address to system devices.

The system shall allow user-defined reporting, including:

System shall store and present system historical data in the form of trend charts and system reports. System software shall allow a for user-defined system reports. User-defined data shall include the monitored assets included in a report, the frequency a report is system generated, and a specific range of data included in a report. System reports shall be displayed in the system software electronically within the interface. System shall allow a system user to print and download reports from the system interface. System shall store archived reports and can be accessed by system users. System shall allow an online method to electronically record the acknowledgment of report reviews completed by system users; to comply with part 11 of Title 21 of the Code of Federal Regulations; Electronic Records; Electronic Signatures (21 CFR Part 11). System shall allow report data to be restricted based on the role(s) assigned to a system user profile.

The system devices shall meet the specifications below:

System devices shall include sensor(s) that measure, log, and monitor [Temperature] [Ambient Temperature and Humidity] [Differential Pressure] conditions. System devices shall be primarily powered by [ac-power] [Power over Ethernet]. System device battery-power shall be used as a backup power source. System devices shall be equipped with monitoring, sampling, logging, alerting, and reporting firmware. System devices can be preconfigured by the Manufacturer with Owner provided settings before shipment to Owner facility or configured locally at the device by the Owner on-site. System device settings are user-defined and are configured in the system software and downloaded to the system devices over the Owner's network. System can be configured to automatically distribute device firmware upgrades at the time system devices connect and communicate to the system or can be configured to allow firmware upgrades to be managed and performed by system users. Each system device shall be identified by a unique MAC address assigned by the Manufacturer. A system device with an external temperature probe shall be NIST traceable and a calibration data report shall be supplied by the Manufacturer. Manufacturer shall offer a temperature probe that links a unique Certificate of Traceability and Calibration Testing to each individual probe within the system software. The certificate shall provide all the data required for compliance to guidelines issued by the CDC and other authorities having jurisdiction. System device firmware shall perform automated diagnostic monitoring of its battery life and strength of the wireless network connection and transmit this data to the system. System devices shall continuously monitor, sample, and log its readings and operating conditions and transmit this data to the system. System devices shall have an audio alert function that can be programed from the system software. System devices shall automatically sample its reading(s) several times a minute and the system device shall continuously log and monitor sampled sensor readings. System devices shall automatically alert and transmit reading data to the system when a sampled readings is not within the user-defined range for 60 consecutive seconds or if a system device is not operating as expected. System devices shall have a LCD screen that displays its battery level, network connection status, and indicate when in an error or alarm state. System temperature sensors LCD screen shall display its last sampled reading, and its Lowest (coldest) Sampled Reading and Highest (warmest) Sampled Reading for its current Collection Period. The Collection Period can be reset locally at the device by an end user. System devices shall have LED indicators, located on the front of the device, that provide a visual indicator of its current status and operating state.

The system devices shall support all of the network communication specifications below:

Network Communication: Wireless Networking Protocols: 802.11b, 11g, single stream 11n, 2.4 Ghz ¦ Security Protocols: WEP, WPA, WPA2 (AES and TKIP) ¦ Encryption Protocols: TLS 1.2¦ Network Communication Protocols: Hypertext Transfer Protocol Secure (HTTPS) ¦ IP Addressing: Dynamic Host Configuration Protocol (DHCP), static IP addressing ¦ Data Packet Size: typically less than 5 kilobytes (kB)* 11n supported by Levo Series Digital Clock/Timer models only.

- The network setting data stored locally in system devices shall be encrypted and access to locally stored data can be controlled by a system admin user.

- Manufacturer shall provide stand-alone configuration software to locally configure a system device to meet Owner security policies if network setting data cannot be stored in third-party software or to troubleshoot device network connectivity issues.

- System devices shall have the ability to store up to 4096 readings locally in device memory to avoid loss of data if a network connectivity issue prevents device data to be transmitted to system software.

- When a system device is operating on battery power and its estimated battery life is less than 25%, the device shall enter an alarm state and transmit its low battery state to the system at its next connection to the system.

1.6 REGULATORY REQUIREMENTS

- Equipment and components furnished shall be of the Manufacturer latest model.

- System devices shall be installed in compliance with local and state authorities having jurisdiction.

- Electrical Components, Devices, and Accessories: Listed and labeled per NFPA 70 by qualified testing agency.

- Regulatory Requirements: System design and installation shall comply with the following: National Electric Code (NEC)

Underwriters Laboratory (UL) standards Local codes and regulations

1.7 SUBMITTALS

- Product Data: Submit complete catalog data for each system device and components, describing physical characteristics and method of installation.

- Shop Drawings: Showing the following. 1. Diagram of proposed monitoring system showing SaaS platform, communication pathway, and schedule of individual system device installation locations. 2. Indicate integration with the Owner's network. Include a line diagram of network relationships. 3. Show system device power requirements.

- Samples: Submit one specified system device model(s) for approval. Approved sample(s) shall be tagged and shall be installed at location directed.

- Manufacturer Instructions: Submit complete installation, set-up and maintenance instructions.

Specifier Note: Informational submittals require review, but no response by A/E or Owner.

- Information submittal: Sample Warranty

- Information submittal: System Subscription Agreement

1.8 SUBSTITUTIONS

- Proposed substitutions, to be considered, shall be manufactured of equivalent materials that meet or exceed specified requirements of this Section.

- Proposed substitutions shall be identified not less than 10 days prior to bid date.

1.9 QUALITY ASSURANCE

- Manufacturer Qualifications: Manufacturer of wireless and Ethernet connected system with a minimum of seven years record of satisfactory manufacturing and support of systems comparable to basis of specified system design.

1.10 DELIVERY STORAGE AND HANDLING

- Deliver all components to the site in the Manufacturer original packaging.

- Packaging shall contain Manufacturer name and address, product identification number, and other related information.

- Store equipment in finished building and in unopened packaging until ready for installation.

1.11 PROJECT SITE CONDITIONS

- System design is integrated with Owner's existing network, including wireless, wired Ethernet, or PoE network.

- Conductors and Cables: Comply with requirements of Division 27 Sections "Common Work

- Results for Communications" and "Communications Horizontal Cabling.

- Signal and Control Circuits: Manufacturer recommended stranded, single conductors, or twisted- pair cables.

- Data Circuits: Category 5 minimum, twisted-pair cable.

- Plenum Cable: Listed and labeled for plenum installation.

1.12 WARRANTY

- Manufacturer will provide a one year limited warranty on all system devices.

- Manufacturer offers an extended warranty on system devices.

1.13 SOFTWARE MAINTENANCE

- Software Maintenance Agreement (SMA): included in the subscription agreement for system.

- All updates, enhancements and maintenance are performed remotely by the Manufacturer per agreed upon SMA.

PART 2 PRODUCTS

2.1 SECTION INCLUDES

- The system and equipment is specified as described in this section.

- All bids shall be based on the equipment as specified herein. The model designations are that of Primex, Inc. The specifying authority must approve an alternate system.

2.2 MANUFACTURER

- System shall be manufactured by:

Primex, Inc. 965 Wells St, Lake Geneva, WI 53147 | Phone: (855) 602-2934 | info@primexinc.com | www.primexinc.com

2.3 SYSTEM SOFTWARE

- Basis of Design Software Product: Primex OneVue™ Environmental Monitoring.

- System Software Platform: Cloud-based software platform that resides on Amazon Web Services (AWS) and is accessed via the internet.

- System stores and monitors system device reading and operational data transmitted over the Owner's network to the system software.

- All system device and system software settings are managed within the cloud-based system software.

2.3 SYSTEM DEVICES & ACCESSORIES

Specifier Note: Primex OneVue sensing devices provide the facility Owner with the ability to monitor and log sensor readings and capture the data without staff interaction, in keeping with facility management best practices and compliance requirements. Accessories are for use with all devices.

Temperature and Humidity Sensor

Specifier Note: Compatible with AC adapter accessories; purchased separately.

Basis of Design Product: PrimexIAQ Temperature and Humidity Sensor ¦ Supplied with battery pack ¦ Part number A100Q Temperature Range and Accuracy: Ambient Temperature Range: 32 to 122 °F (0 to 50 °C) ¦ Ambient Temperature Accuracy: ± 1.0 °F (±-0.5 °C) between 32 °F and 122 °F (0 °C and 50 °C) Humidity Range and Accuracy: Humidity Range: 0% to 100% RH ¦ Humidity Accuracy: ± 3% RH for range of 20% to 80% RH, ± 5% outside of range Network Communication: Wireless Networking Protocols: 802.11b, 11g, single stream 11n, 2.4 Ghz ¦ Security Protocols: WEP, WPA, WPA2 (AES and TKIP) ¦ Encryption Protocols: TLS 1.2¦ Network Communication Protocols: Hypertext Transfer Protocol Secure (HTTPS) ¦ IP Addressing: Dynamic Host Configuration Protocol (DHCP), static IP addressing ¦ Data Packet Size: typically less than 5 kilobytes (kB) Enclosure: ABS plastic ¦ Dimension: 4.7" H x 3.7" W x 1.3" D (11.93cm x 9.39cm x 3.30cm) ¦ Weight: 0.3 lb (136 gram) with 2 AA batteries Display: Liquid crystal display (LCD), dimension: 0.75 in. H x 1.38 in. W (1.90 cm x 3.50 cm) ¦ LED Status Indicator: green, yellow, red Mounting: Keyhole slot with lock down screw holes in back panel for wall mount; or surface mount with supplied dual-lock adhesive mounting strips. Operation: Alerts: audio, visual LED, LCD display ¦ Audio Alert Resume Period (user-defined): Next alarm, 15min, 30min, 1hr, 2hr, 3hr, 4hr Configuration: configured from system software or locally at device with supplied device configuration software Stored Reading Capacity: 4096 readings Check-in Interval and Logging Interval settings (user-defined): 4min, 5min, 10min, 15min,20min, 30min, 1hr, 2hr, 3hr, 4hr, 8hr, 12hr Battery-power: 3.0v Primex Lithium/Iron Disulfide Battery Pack or two stand-alone 1.5v Lithium AA batteries. ¦ Use of alkaline batteries is not recommended ¦ Estimated battery life: Up to 18 months with use of Lithium 1.5V batteries; estimation based on 1 hour logging interval, 8 hour check-in interval and adequate wireless signal. Environment: Operating Temperature: 32 to 122° F (0 to 50° C), indoor use only ¦ Storage Temperature: -4 to 140 ° F (-20 to 60° C) Certifications: FDA registered, CFR Part 11 compliant ¦ FCC, CE, and IC compliant

Temperature Sensor - Single Probe

Specifier Note: Compatible with AC adapter accessories; purchased separately.

Basis of Design Product: PrimexTEMP Series Device Single Probe ¦ Supplied with battery pack ¦ Part Number T101Q Basis of Design Product: PrimexTEMP Series Device Single Probe Power over Ethernet (PoE) model ¦ Compliant with IEEE 802.3af standard and compatible with 802.3at standard ¦ Supplied with battery pack ¦ Part Number T101Q-E Network Communication: Wireless Networking Protocols: 802.11b, 11g, single stream 11n, 2.4 Ghz ¦ Security Protocols: WEP, WPA, WPA2 (AES and TKIP) ¦ Encryption Protocols: TLS 1.2¦ Network Communication Protocols: Hypertext Transfer Protocol Secure (HTTPS) ¦ IP Addressing: Dynamic Host Configuration Protocol (DHCP), static IP addressing ¦ Data Packet Size: typically less than 5 kilobytes (kB) Enclosure: ABS plastic ¦ Dimension: 4.7" H x 3.7" W x 1.3" D (11.93cm x 9.39cm x 3.30cm) ¦ Weight: 0.3 lb (136 gram) with 2 AA batteries Display: Liquid crystal display (LCD), dimension: 0.75 in. H x 1.38 in. W (1.90 cm x 3.50 cm) ¦ LED Status Indicator: green, yellow, red Mounting: Keyhole slot with lock down screw holes in back panel for wall mount; or surface mount with supplied dual-lock adhesive mounting strips. Operation: Alerts: audio, visual LED, LCD display ¦ Audio Alert Resume Period (user-defined): Next alarm, 15min, 30min, 1hr, 2hr, 3hr, 4hr Configuration: configured from system software or locally at device with supplied device configuration software Stored Reading Capacity: 4096 readings Check-in Interval and Logging Interval settings (user-defined): 4min, 5min, 10min, 15min,20min, 30min, 1hr, 2hr, 3hr, 4hr, 8hr, 12hr Battery-power: 3.0v Primex Lithium/Iron Disulfide Battery Pack or two stand-alone 1.5v Lithium AA batteries. ¦ Use of alkaline batteries is not recommended ¦ Estimated battery life: Up to 18 months with use of Lithium 1.5V batteries; estimation based on 1 hour logging interval, 8 hour check-in interval and adequate wireless signal. Environment: Operating Temperature: 32 to 122° F (0 to 50° C), indoor use only ¦ Storage Temperature: -4 to 140 ° F (-20 to 60° C) Certifications: FDA registered, CFR Part 11 compliant ¦ FCC, CE, and IC compliant

Temperature Sensor - Dual Probe

Specifier Note: Compatible with AC adapter accessories; purchased separately.

Basis of Design Product: PrimexTEMP Series Dual Probe Sensor with wireless technology¦ Supplied with backup battery pack ¦ Part number T102Q Basis of Design Product: PrimexTEMP Series Dual Probe Sensor Power over Ethernet (PoE) model; compliant with IEEE 802.3af standard and compatible with 802.3at standard ¦ Supplied with backup battery pack ¦ Part number T101Q-E Network Communication: Wireless Networking Protocols: 802.11b, 11g, single stream 11n, 2.4 Ghz ¦ Security Protocols: WEP, WPA, WPA2 (AES and TKIP) ¦ Encryption Protocols: TLS 1.2¦ Network Communication Protocols: Hypertext Transfer Protocol Secure (HTTPS) ¦ IP Addressing: Dynamic Host Configuration Protocol (DHCP), static IP addressing ¦ Data Packet Size: typically less than 5 kilobytes (kB) Enclosure: ABS plastic ¦ Dimension: 4.7" H x 3.7" W x 1.3" D (11.93cm x 9.39cm x 3.30cm) ¦ Weight: 0.3 lb (136 gram) with 2 AA batteries Display: Liquid crystal display (LCD), dimension: 0.75 in. H x 1.38 in. W (1.90 cm x 3.50 cm) ¦ LED Status Indicator: green, yellow, red Mounting: Keyhole slot with lock down screw holes in back panel for wall mount; or surface mount with supplied dual-lock adhesive mounting strips. Operation: Alerts: audio, visual LED, LCD display ¦ Audio Alert Resume Period (user-defined): Next alarm, 15min, 30min, 1hr, 2hr, 3hr, 4hr Configuration: configured from system software or locally at device with supplied device configuration software Stored Reading Capacity: 4096 readings Check-in Interval and Logging Interval settings (user-defined): 4min, 5min, 10min, 15min,20min, 30min, 1hr, 2hr, 3hr, 4hr, 8hr, 12hr Battery-power: 3.0v Primex Lithium/Iron Disulfide Battery Pack or two stand-alone 1.5v Lithium AA batteries. ¦ Use of alkaline batteries is not recommended ¦ Estimated battery life: Up to 18 months with use of Lithium 1.5V batteries; estimation based on 1 hour logging interval, 8 hour check-in interval and adequate wireless signal. Environment: Operating Temperature: 32 to 122° F (0 to 50° C), indoor use only ¦ Storage Temperature: -4 to 140 ° F (-20 to 60° C) Certifications: FDA registered, CFR Part 11 compliant ¦ FCC, CE, and IC compliant Standard Probe ¦ Range: -40 °C to 105 °C (-40°F to 221 °F) Specifier Note: For use with PrimexTEMP sensors The PrimexPROBE with CertiTrak Calibration Certification Tracking eliminates the need to manually track calibration data and probe life of temperature monitoring probes. Using patent-pending technology, each probe activates CertiTrak when the probe is initially inserted into a PrimexTEMP sensor and put into service. Basis of Design Product: PrimexPROBE with CertiTrak ¦ Part number T100SMRT Temperature Range: -40 °C to 105 °C (-40°F to 221 °F) Accuracy: ± 0.5 °C (1° F) Sheath Material: stainless steel Sheath Length: 4 in. (10.1 cm) Sheath Diameter: 1/4 in. (0.63 cm) Cable Properties: ribbon Cable Length: 6 feet (1.8 m)

Extended Range (cryogenic) Probe | Range: 200 °C to 150 °C (-328°F to 238°F)

Specifier Note: For use with PrimexTEMP sensors The PrimexPROBE with CertiTrak Calibration Certification Tracking eliminates the need to manually track calibration data and probe life of temperature monitoring probes. Using patent-pending technology, each probe activates CertiTrak when the probe is initially inserted into a PrimexTEMP sensor and put into service.

Basis of Design Product: PrimexPROBE Cryo with CertiTrak ¦ Part number T100CSMRT Temperature Range: -200 °C to 150 °C (-328°F to 238°F) Accuracy: ± 0.5 °C (1° F) Sheath Material: stainless steel Sheathe Length: 4 in. (10.1 cm) Sheath Diameter: 1/4 in. (0.63 cm) Cable Properties: nylon Cable Length: 6 feet (1.8 m)

Thermobuffer

Specifier Note: For use with PrimexTEMP sensors. Thermobuffer is offered in a Solid Wax Based Thermobuffer and a Thermobuffer with use with Food Grade Glycol. The models are specific to the probe assembled with the Thermobuffer as specified below. Thermobuffer is a 2 oz (60 ml) bottle.

Basis of Design Product: Solid Wax Based Thermobuffer assembled with PrimexPROBE with CertiTrak T100SMRT ¦ Part number SMRTGRP-C Basis of Design Product: Glycol Thermobuffer assembled with PrimexPROBE with CertiTrak T100SMRT ¦ Part number SMRTGRP-G Basis of Design Product: One (1) Gallon of Food Grade Glycol ¦ Part number SNSGLY-1 Basis of Design Product: Glycol Bottle (probe sold separately) ¦ Part number SNSGRP Differential Pressure Sensor Specifier Note: Model is available in AC or PoE; backup battery pack is supplied. Basis of Design Product: PrimexIAQ Differential Pressure Sensor ¦ Part number A120Q ¦ Supplied with AC-power adapter and backup battery pack. Basis of Design Product: PrimexIAQ Differential Pressure Sensor Power over Ethernet (PoE) model ¦ Compliant with IEEE 802.3af standard and compatible with 802.3at standard ¦ Supplied with battery pack ¦ Part number A120Q-E Provides readings in inches of water (inches H2O) or Pascals (Pa). Full measurement range is ± .001 to 0.500 inches H2O (± 2.0 to 125 Pa). Includes two 6 feet (1.82 m) lengths of silicone tubing with 1/4 in. (6.35 mm) O.D./1/8 in. (3.17 mm) I.D. Network Communication: Wireless Networking Protocols: 802.11b, 11g, single stream 11n, 2.4 Ghz ¦ Security Protocols: WEP, WPA, WPA2 (AES and TKIP) ¦ Encryption Protocols: TLS 1.2¦ Network Communication Protocols: Hypertext Transfer Protocol Secure (HTTPS) ¦ IP Addressing: Dynamic Host Configuration Protocol (DHCP), static IP addressing ¦ Data Packet Size: typically less than 5 kilobytes (kB) Enclosure: ABS plastic ¦ Dimension: 4.7" H x 3.7" W x 1.3" D (11.93cm x 9.39cm x 3.30cm) ¦ Weight: 0.3 lb (136 gram) with 2 AA batteries Display: Liquid crystal display (LCD), dimension: 0.75 in. H x 1.38 in. W (1.90 cm x 3.50 cm) ¦ LED Status Indicator: green, yellow, red Mounting: Keyhole slot with lock down screw holes in back panel for wall mount; or surface mount with supplied dual-lock adhesive mounting strips. Operation: Alerts: audio, visual LED, LCD display ¦ Audio Alert Resume Period (user-defined): Next alarm, 15min, 30min, 1hr, 2hr, 3hr, 4hr Configuration: configured from system software or locally at device with supplied device configuration software Stored Reading Capacity: 4096 readings Check-in Interval and Logging Interval settings (user-defined): 4min, 5min, 10min, 15min,20min, 30min, 1hr, 2hr, 3hr, 4hr, 8hr, 12hr Battery-power: 3.0v Primex Lithium/Iron Disulfide Battery Pack or two stand-alone 1.5v Lithium AA batteries. ¦ Use of alkaline batteries is not recommended ¦ Estimated battery life: Up to 18 months with use of Lithium 1.5V batteries; estimation based on 1 hour logging interval, 8 hour check-in interval and adequate wireless signal. Environment: Operating Temperature: 32 to 122° F (0 to 50° C), indoor use only ¦ Storage Temperature: -4 to 140 ° F (-20 to 60° C) Certifications: FDA registered, CFR Part 11 compliant ¦ FCC, CE, and IC compliant

Accessories

Specifier Note: Only include those accessories specified.

AC adapter ¦ 5V DC USB Mini B (5 pin) connector interface ¦ 2. 5 feet (1.5 m) cable ¦ Input: 100-240 VAC, 50/60 Hz ¦ Output: 5V, 1.0A max ¦ Part number S100PWR AC Adapter Extension ¦ 6 feet (1.8M) ¦ part number Q13827 Battery Pack Replacement ¦ 3.0v Lithium/Iron Disulfide Battery Pack (contains 2 AA 1.5V Energizer® Ultimate Lithium batteries) ¦ Part number SNS900 Temp Probe Extension ¦ 6 feet (1.8 m )¦ Part number Q13824-6 Temp Probe Extension ¦25 feet (7.6 m) ¦ Part number Q13824-25 For use with Differential Pressure sensor: Magnetic Door Switch with 25 feet (7.6 m) cable ¦ Part number SNSMSW1 Differential Pressure Installation Kit: Includes 2 stainless steel wall plates, tapered nozzle and screen pickup accessory for through-wall installations, 2 sealing rubber grommets, static pressure tip for placement in duct or through-the-wall installations ¦ Part number SNSDPLT

PART 3 EXECUTION

3.1 EXAMINATION

- Examine conditions with the Installer present for compliance with requirements and other conditions affecting the performance of the system and system devices.

- Do not proceed until unsatisfactory conditions have been corrected.

- Verify that construction is complete in spaces to receive equipment and that rooms are clean and dry.

3.2 INSTALLATION

- General: Install system devices in accordance with applicable codes.

- Install system devices in accordance with Manufacturer written instructions.

- Provide all system equipment necessary for a complete and operable system.

- Comply with requirements of Division 27 Sections "Common Work Results for Communications" and "Communications Horizontal Cabling."

- Cables: Install cables in raceways and cable trays except within consoles, cabinets, and desks [and except in accessible ceiling spaces and framed partitions where exposed wiring is allowed by Owner]. Install plenum cable where required. Conceal cable installation where possible.

3.3 FIELD INSPECTION

- Inspection: Make observations to verify that system devices and components are properly labeled.

- Prior to final acceptance, inspect each system device and component, adjust as required, and replace parts which are found defective.

- At completion of system device installation and prior to final acceptance, turn on the equipment; ensure that all equipment is operating properly, and that the system software and all system devices and components are functioning.

3.4 SERVICES

- Manufacturer system software user guides and system device installation guides shall be provided electronically within system software.

- Commissioning General: Provide system commissioning in accordance with Manufacturer written recommendations. Perform operational testing to verify compliance with requirements. Adjust as required.

- Services shall include specified level of commissioning services.

Specifier Note: Only include one level of the available commissioning services identified below. Contact Primex for additional information.

Phone commissioning service: system deployment training, including system set up, validation of device preconfiguration, and system functionality by way of remote web conference. On-site commissioning service: system deployment training, including system set up, validation of device preconfiguration, system functionality, verification of device network connections, and device installation training. Installation and full on-site commissioning service: system training, software configuration, validation of device preconfiguration, training on system functionality, verification of network use, device installation training, and device installation.

3.5 CLEANING

- Prior to final acceptance, clean exposed surfaces of devices, using cleaning methods recommended by Manufacturer.

3.6 DEMONSTRATION

- Initial Demonstration and Training: provide demonstration and training for Owner facility staff that is responsible to perform system software administration.

- Demonstrate maintenance procedures for system devices.

- Demonstrate the system software components and features, including monitoring and management of system devices.

3.7 PROTECTION

- Protect finished installation until final acceptance of the project.

3.8 TESTING

- All system devices must be tested at their operational installation location under normal operational conditions.