Product Specification

28 47 00 Mass Notification

Primex OneVue™ Notify Critical Notification System

Last update: 7/28/2026

Specifier Note: This product specification is written according to the Construction Specifications Institute (CSI), MasterFormatTM, SectionFormat, and PageFormat, contained in the CSI Manual of Practice. The section must be carefully reviewed and edited by the Architect/Engineer/Consultant to meet the requirements of the project and local building code. Coordinate this section with other specification sections and the drawings. Delete all “Specifier Notes” when editing this specification.

PART 1 GENERAL

1.1 GENERAL REQUIREMENTS & SCOPE

The system is specified as described.

- Furnish and install a complete new Critical Notification System using the Primex OneVue™ Notify platform.

- Furnish and install all system devices, accessories, and material in accordance with these specifications and drawing to provide a complete and operating system.

- All bids shall be based on the equipment as specified herein. The model designations are that of Primex, Inc. The specifying authority must approve any alternate system

Specifier Note: Edit the following system devices and accessories as required for the project.

- System shall include the following system devices:

OneVue Sync Transmitter [1 Watt with Internal Antenna] [1 Watt with External Antenna] [5 Watt Transmitter] [30 Watt Transmitter]

OneVue Sync Repeater Transmitter

External Antenna [Non-penetrating Mast Antenna Kit] [Penetrating Mast Antenna Kit]

GPS Receiver

GPS Extension Cables [50 ft] [100 ft] [200 ft] (200 ft maximum length)

Digital display devices and accessories

  - Large InfoBoard with audible tone

  - Medium InfoBoard with audible tone

  - Mini InfoBoard

  - Critical Notification Panel

1.2 RELATED SECTIONS

Specifier Note: Edit the following list as required for the project. List other sections with work directly related to this section.

- Division 26 “Electrical”

- Division 26 Section “Common Work Results for Electrical”

- Division 27 Section "Common Work Results for Communications"

- Division 27 Section "Communications Horizontal Cabling"

- 27 53 13 Wireless Clock System

- 27 51 23.50 Educational Intercommunications and Program Systems

1.3 REFERENCES

System devices specified shall meet or exceed the requirements of the following.

Specifier Note: List standards referenced in this section, complete with designations and titles. This article does not require compliance with standards, but is merely a list of those used.

- National Fire Protection Association (NFPA): 1. NFPA 70 - National Electrical Code (NEC).

- Manufacturer Installation and User Guides.

1.4 DEFINITIONS

This section provides commonly used terms within this specification.

- SaaS: Software-as-a-Service

- AWS: Amazon Web Services

- TLS: Transport Layer Security

- HTTPS: Hypertext Transfer Protocol Secure

- SSA: Software Subscription Agreement

- SMA: Software Maintenance Agreement

- System user: a user profile in the system software; grants access software features and data by way of user role(s) assigned to each system user.

1.5 SYSTEM DESCRIPTION

Specifier Note: System description is based on the Primex OneVue Notify platform. System options: - OneVue Notify Monitor (Transmitter and InfoBoards/MiniBoards): Digital Critical Notifications, Digital Non-critical Messaging, and Synchronized Time. Devices can also operate as a Schedule Countdown Timer, Code Blue Timer with Timer Switch Control, and Elapsed Timer with Timer Switch Control. Provides InfoBoard/MiniBoard advanced setting management through OneVue cloud-based software. Requires OneVue Software Subscription Agreement and Transmitter, InfoBoards, and MiniBoards require an Ethernet connection to OWNER network. - OneVue Notify Standalone (Transmitter and InfoBoards/MiniBoards): Digital Critical Notifications, Synchronized Time, Code Blue Timer with Timer Switch Control, Elapsed Timer with Switch Control Timer. Transmitter, InfoBoard, and MiniBoard limited setting management through OneVue Device Configurator (ODC) mobile app. *System can be integrated with the OneVue Notify Bell Scheduling (27 51 23.50 Educational Intercommunications and Program Systems) and OneVue Sync solution (27 53 13 Wireless Clock System)

General Specifications

- System shall provide a fully operational one-way, visual digital critical communication notification system, by way of the system's digital display devices that receive critical notification events from system transmitters.

- System transmitter devices shall operate over a 72MHz wireless radio frequency that efficiently broadcasts signals through commercial building materials to ensure the system digital display devices equipped with 72MHz technology receive critical notification events and time/date information.

- System shall require a Call Sign [U.S. FCC] [Canada ISED] license for transmitter operation over the 72MHz wireless radio frequency resulting in a safe and interference free operation.

- System transmitters can be configured with a variety of power output levels to provide coverage for a single building or an entire campus.

- System main transmitter shall provide a contact closure method to broadcast critical communication events to the system digital display devices.

- System digital display devices shall provide accurate, synchronized time when not displaying critical notification events.

- System shall include a Manufacturer supplied five button contact closure control switch (critical notification panel) that is hardwired to the main transmitter contact closure event panel.

  - Critical communication events are activated by pressing of a critical notification panel button by an end-user, or by an integrator system capable of activating contact closure events through an auxiliary jack that is wired to the main transmitter contact closure panel.

  - Transmitter contact closure panel shall be capable of either normally closed or normally opened position.

- System digital display devices shall allow five predefined notification events;

Specifier Note: These settings can be customized with the OneVue Monitor Notify system.

- (1) Lockdown, LED Color: Red, Mode: Flashing, Scroll: 0 (none)

- (2) Evacuate, LED Color: Blue, Mode: Flashing, Scroll: 0 (none)

- (3) Weather, LED Color: Yellow, Mode: Flashing, Scroll: 0 (none)

- (4) Lockout, LED Color: White, Mode: Constant, Scroll: 2

- (5 Preset Off) All Clear, LED Color: Green, Mode: Constant, Display Duration: 5 minutes

- System digital display devices shall have three color LED options when displaying time/date data including red, green, and white.

- System shall provide synchronized time wirelessly from a system transmitter to digital display devices when not displaying critical notification events. The system main Transmitter time source can either be from a GPS Receiver, an internal NTP Server or an external NTP server over port 123. NTP time requires main transmitter access to the OWNER'S Ethernet network.

- System shall provide a mobile iOS and Android™ app to on-board system devices and manage system devices' primary settings.

- System shall allow system transmitters to be monitored from system software at no charge to allow remote support services. System software shall allow management of transmitter settings.

- System device firmware revisions shall be provided under the system purchase agreement.

- System shall not require the installation of any on-site system hardware or software, with the exception of the system devices and accessories, external GPS time source, and transmitter external antenna components.

- (HEALTHCARE) Digital display devices shall have the ability to function as a Code Blue Timer by integrating with the OWNER'S existing (supported) code blue control system.

  - Device supports code blue systems that apply a voltage to start a code blue event or code blue systems that use a dry contact and do not inject a voltage.

  - Code Blue configuration shall include a Manufacturer supplied three button wall mountable Timer Control Switch. Required to be mounted in a single gang electrical box (not supplied).

  - Timer Switch Control connected to device with a supplied reversed wire (cross-pinned) telephone cable with an RJ-11 connector. Cable can be extended up to 100 ft. (30.48 m).

  - Timer Switch Control switch can be configured to simultaneously activate two connected devices.

  - Timer Switch Control and buttons must be a cleanable surface with use common disinfectants.

SPECIFIER NOTE: Include this section for: OneVue Notify Monitor - requires Software Subscription Agreement.

System Remote Management & Monitoring

- System shall be licensed and delivered via a Software-as-a-Service (SaaS) model, in which the system software is licensed on a subscription basis hosted by Manufacturer, and is delivered to OWNER as a cloud-based software powered by Amazon Web Services (AWS).

- Manufacturer shall offer subscription pricing models, which are to be inclusive of software access, technical support, enhancements, and software maintenance.

- System software shall be accessed from a web browser on a mobile or tablet device or computer with an internet connection, and does not require the installation of software or other third-party plug-ins or applications.

- System shall require that all system digital display devices to have an Ethernet connection to the OWNER Local Area Network (LAN) via the device's Ethernet port. All system software network and port requirements are to be met to allow connection to system software.

- System software shall maintain and store redundant, data backups for up to a minimum of 7 years.

- System software shall allow authorized system users to customize the five critical communication events; including 64 character event text, LED display color, mode flashing or constant, and scrolling speed. Critical Notification Panel button labels can be updated by OWNER to align with event text.

- System software shall allow authorized system user to manage digital display device settings; including display brightness level, time color, timer color, date color, date format, message color, message scroll speed, 64-character non-critical digital message, and display interval (show, display date for number of seconds, display message for number of seconds).

- System shall also provide a fully operational one-way, user-defined non-critical 64 character digital message to be displayed by the digital display devices when not displaying critical notification events.

  - Digital messages are managed from the system software; settings include alpha-numeric and special characters message, digit color, and scroll speed.

- System digital display device setting changes shall be downloaded to devices at a minimum of every five minutes over the device's connection to system OWNER Ethernet network.

- System digital display devices shall connect to OWNER Ethernet network and system software once a day at a system defined time to report its events, diagnostic and status data, and download pending firmware updates and receive synchronized time.

- System software shall receive and store system device event logs showing the event type, time, and date records.

- System software shall monitor and display the operating status transmitted by system devices to the system software.

- System software shall allow authorized system users to view monitoring data, including operating condition of the system devices, and historical device operating condition and event data transmitted to system software.

- System software shall allow authorized system users to view and manage system device settings

- System software shall generate text (SMS), email and voice alert messages when a system transmitter device operating condition may warrant corrective action or maintenance.

  - Generate alert messages to system users 24 hours a day, 365 days a year based on staffing schedules

  - Allows system users the ability to acknowledge an alert within the system software or by voice alert message.

  - System software shall record and store the history of all alerting data and system user actions.

- System software shall provide a method to generate automated reports that notify system users when a digital display device may warrant corrective action or maintenance.

- System software shall provide a single dashboard view that displays the current state of system devices, active alerts, and system announcements.

- System software shall allow system users to customize data views within their system user account.

- System software shall allow a system user admin(s) to grant and control the data and features available to system users, view user log in history, and set system wide user password complexity settings and session timeout settings.

- System software shall allow each system user to manage their own system profile; specifying the method(s) of preference in which they receive alert notifications, user profile log in email address and password, and contact settings.

- System software shall allow user-defined reporting; store and present system historical data in the form of system reports.

  - User-defined data including system devices included in a report, the frequency a report is system generated, and a specific range of data included in a report, and system users to receive report notifications.

  - System shall allow an online method to electronically record the acknowledgment of report reviews completed by system users; to comply with part 11 of Title 21 of the Code of Federal Regulations; Electronic Records; Electronic Signatures (21 CFR Part 11).

- System software shall provide a method to group digital display devices to allow standardized settings for all or a subset of devices.

- System software shall monitor system devices connection to system software.

  - When a system transmitter connection is not detected for a user-defined specified time period, the system shall generate an alert notification to user-defined system users.

  - When a system digital display connection is not detected for a user-defined specified time periods, the system shall include the device in the system user-defined reports.

- System device firmware shall be provided under the Manufacturer Software Subscription Agreement and managed by automatic over-the-air (OTA) updates or by a system user either from the system software or system mobile configurator app.

  - System device firmware shall perform diagnostics on time accuracy and transmits this data to system software.

- (EDUCATION) Digital display devices shall have the ability to function as a Schedule Countdown Timer.

  - Scheduled count mode is activated by zone (schedule), assigned to digital display devices, that is managed from system software.

  - Schedule to allow up to a maximum of 48 individual events.

  - Schedule allows audible ring types and allow system users to create customized ring types. Audible tones are dependent on digital display device model.

  - Exception count-down schedules that override a default schedule for a specified date range.

  - Digital event devices shall connect to system software daily to update its 7-day count-down schedule.

- (HEALTHCARE or EDUCATION) Digital display devices shall have the ability to function as Elapsed Timer.

  - Elapsed Timer mode is triggered with the Manufacturer supplied three button Timer Control Switch.

  - An audible tone option set in system software for count stop event. Audible option dependent on device model.

  - Accurately count up or count down up to a maximum of 99 hours, 59 minutes, and 59 seconds.

  - Timer Control Switch required to be mounted in a single gang electrical box.

  - Timer Control Switch connects to device with a supplied reversed wire (cross-pinned) telephone cable with an RJ-11 connector and cable can be extended up to maximum of 100 ft. (30.4 m).

  - Timer Control Switch can be wired to simultaneously activate two connected devices.

  - Control switch buttons are washable with water and common disinfectants.

- (EDUCATION) Digital display devices also shall have the capability to emit an audible tone for scheduled events using the system software zone schedules. For integration with other PA or Bell schedule systems, the use of the system Bell Controller assigned to the same schedules is required. Note that audible tones are only available on Medium and Large InfoBoards.

Network Encryption and Authentication

- All system user sessions between the web browser and the system software shall be encrypted by the HTTPS protocol.

- All client and device data is encrypted in transmit and all sensitive data is encrypted at rest. An outbound HTTPS connection is established by each device and once complete the IP address is released.

- The network setting data stored locally in system devices shall be encrypted and access to locally stored data can be controlled by a system admin user.

- Port UDP 123: used by Power over Ethernet (PoE)/Ethernet devices to access an external NTP Server. Port is required to be open for use with external Network Time Protocol (NTP) Servers. Use of internal NTP Servers is also supported.

- Remote Monitoring and Management use: Organizations with network firewalls in place must proactively allow outbound network communication and file downloads through specific system software Domains and URLs.

1.6 REGULATORY REQUIREMENTS

- Equipment and components furnished shall be of the Manufacturer latest model.

- System devices shall be installed in compliance with local and state authorities having jurisdiction.

- Electrical Components, Devices, and Accessories: Listed and labeled per NFPA 70 by qualified testing agency.

- Regulatory Requirements: System design and installation shall comply with the following: National Electric Code (NEC)

- Underwriters Laboratory (UL) standards - Local codes and regulations

1.7 SUBMITTALS

- Product Data: Submit complete catalog data for each system device and components, describing physical characteristics and method of installation.

- Shop Drawings: Showing the following. 1. Diagram of proposed system showing communication pathway, and schedule of individual system device installation locations. 2. Indicate integration with the OWNER'S network. Include a line diagram of network relationships. 3. Show system device power requirements.

- Samples: Submit one specified system digital display model(s) for approval. Approved sample(s) shall be tagged and shall be installed at location directed.

- Manufacturer Instructions: Submit complete installation, set-up and maintenance instructions.

Specifier Note: Informational submittals require review, but no response by A/E or Owner.

- Information submittal: Sample Warranty

- Information submittal: Software Subscription Agreement (SSA)

1.8 SUBSTITUTIONS

- Proposed substitutions, to be considered, shall be manufactured of equivalent materials that meet or exceed specified requirements of this Section.

- Proposed substitutions shall be identified not less than 10 days prior to bid date.

1.9 QUALITY ASSURANCE

- Manufacturer Qualifications: Manufacturer of wireless and Ethernet connected system with a minimum of fifteen years record of satisfactory manufacturing and support of systems comparable to basis of specified system design.

1.10 DELIVERY STORAGE AND HANDLING

- Deliver all components to the site in the Manufacturer original packaging.

- Packaging shall contain Manufacturer name and address, product identification number, and other related information.

- Store equipment in finished building and in unopened packaging until ready for installation.

1.11 PROJECT SITE CONDITIONS

- System design is integrated with OWNER'S existing wired Ethernet network.

- Conductors and Cables: Comply with requirements of Division 27 Sections "Common Work

- Results for Communications" and "Communications Horizontal Cabling.

- Signal and Control Circuits: Manufacturer recommended stranded, single conductors, or twisted- pair cables.

- Data Circuits: Category 5 minimum, twisted-pair cable.

- Plenum Cable: Listed and labeled for plenum installation.

1.12 WARRANTY

- Manufacturer will provide a five year limited warranty on Transmitter(s).

- Manufacturer will provide a two year limited warranty on InfoBoards/MiniBoards.

1.13 SOFTWARE MAINTENANCE

Specifier Note: Include section only for OneVue Notify Monitor system.

- System software maintenance included in the system Software Subscription Agreement (SSA).

- All software updates, enhancements, and maintenance are performed remotely by the Manufacturer.

PART 2 PRODUCTS

2.1 SECTION INCLUDES

- The system and equipment is specified as described in this section.

- All bids shall be based on the equipment as specified herein. The model designations are that of Primex, Inc. The specifying authority must approve an alternate system.

2.2 Manufacturer

- System shall be manufactured by:

Primex, Inc. 965 Wells St, Lake Geneva, WI 53147 | Phone: 1-855-602-2934 | info@primexinc.com | www.primexinc.com

2.3 SYSTEM OPERATION

The system shall perform in the sequence of operation as described.

- Configure and install system appliance detailed in Manufacturer installation instructions.

- Configure and install system devices per model specifications detailed in Manufacturer installation instructions.

- System transmitter required to be configured with a [U.S. FCC] [Canada ISED] Call Sign license to broadcast over the 72MHz frequency.

Transmitter Operation

- When power is first applied to the transmitter, it checks its settings, contact closure inputs, and obtains UTC time from its time source.

- When a contact closure event is invoked, automatically broadcasts the event to system digital display devices.

Master Time Source Operation

Specifier Note: Only include one system specified master time source. With the OneVue Notify Monitor subscription an InfoBoard/MiniBoard can be configured to receive time directly from an NTP Server through an Ethernet connection, or through receiving time from a system Transmitter that can provide a higher level of accuracy by more frequent synchronization and is recommend by Primex.

- Transmitter GPS Time Source: When system main transmitter is in GPS mode, it powers to a connected GPS module mounted with a clear view of the sky. Upon power the GPS module seeks the GPS satellites in orbit to determine position and UTC time. Once the transmitter acknowledges receivable GPS data, it downloads time data and synchronizes its internal master clock to GPS time. The transmitter then starts to broadcast its internal time once every second. The transmitter updates its internal clock every time it receives valid time data from GPS time source.

- Transmitter NTP Time Source: With the system main transmitter is in NTP mode, it connects to the OWNER Ethernet network to the IP address of the NTP server. This IP address is programmed into the transmitter as part of its configuration. Once the connection to the NTP server is acknowledged, it downloads UTC time and synchronizes to its internal master clock to its configured time zone. The transmitter then starts to broadcast its internal time once every second. The transmitter updates its internal clock in this mode once per hour.

- Digital Display Device NTP Time Source: Each device connects to OWNER Ethernet network, once a day at a system specified time, to its configured NTP time source (set in system software) and then synchronizes its time to NTP time received and time zone offset.

Critical Communication Event Operation

- After initial setup, digital event device receiver remains continuously on to receive broadcasted events from a system transmitter.

- When an event is received, the device displays the event until an all clear event is received.

Non-critical Digital Message Event Operation

- After initial setup, digital event device downloads message settings from system software over its connection to OWNER Ethernet network and displays message at user-defined settings.

- At a minimum of every five minutes devices connect to OWNER Ethernet to download pending setting updates from system software.

2.4 EQUIPMENT

The system shall include all equipment as specified.

Transmitter Equipment

- Internal clock: Transmitter shall contain an internal clock such that failure to update time from time source will not disable the operation secondary system devices.

- Transmitter settings shall be managed by the OWNER from the system mobile configurator app or system software. Mobile app user-specified settings include transmit schedule continuously after power up (0 to 23 hours), Normal Transmit schedule (1 to 24 hours), and Repeater Transmitter RF Channel and Repeater Channel.

- Time Zone (all time zones in the world). Includes: Eastern, Central, Mountain, Pacific, Alaska, and Hawaii), Daylight Saving Time bypass option, 12-hour or 24-hour display, GPS or NTP time source, Local or LAN configuration, UTC+ or UTC-, 30 minute UTC offset option CANADA (for Newfoundland). Use of 72MHz frequency may be limited in some international geographic regions.

- [U.S. FCC] [Canada ISED] Call Sign License: Transmitter Call Sign and channel set by the Manufacturer at time of purchase. Call Sign, channel number, and time zone predetermined during licensing process based on OWNER location and existing wireless services operating in the area. OWNER required to contact Manufacturer if, for any reason, a different broadcast channel or time zone ; request requires a modification of the license, requiring approval by [U.S. FCC] [Canada ISED].

- Per specification supply following model(s).

Specifier Note: Select Transmitter model 1 Watt, 5 Watt, or 30 Watt. Optional Repeater Transmitter to extend coverage. A Primex Site Survey is required prior to specifying system.

| Model | Antenna | Time Source | Part No |
| --- | --- | --- | --- |
| OneVue Sync 1 Watt Transmitter | Internal | NTP or GPS | TX4001IM |
| OneVue Sync Watt Transmitter | External | NTP or GPS | TX4001EM |
| OneVue Sync 5 Watt Transmitter | External | NTP or GPS | TX4005EM |
| OneVue Sync 30 Watt Transmitter | External | NTP or GPS | TX40030EM |
| OneVue Sync Repeater Transmitter (1 Watt) | Internal | Main transmitter | TX4001NR |

Transmitter 1 Watt

Transmitter shall meet the specifications below:

- Operating Frequency Range: 72MHz (Call Sign set to [U.S. FCC] [Canada ISED] license)

- 1 Watt maximum transmission (at transmitter)

- Channels: 49 (set to [U.S. FCC] [Canada ISED] license)

- AC power supply: Input: 120 VAC, 50/60 Hz, 0.6 Amp, Output: 9 VDC, 2.78 Amp, 6 ft. (1.83 m) cord.

- Bluetooth® Wireless Communication Protocol: Bluetooth® Low Energy (BLE) Wireless Technology, version 4.1

- Front panel: Four LED status indicators (Power, Transmit, Caution, Error) and Bluetooth labeled push-button to pair with the Primex OneVue Device Configurator (ODC) app.

- Rear panel: Network LAN port (RJ-45 Ethernet, 100/10 Mbps, 802.3 Ethernet), GPS In port (MiniDIN 7-Pin), External Antenna connector (coaxial, n-male), Baseboard Monitor port MiniDIN 9-Pin for use with 5 or 30 Watt Transmitter only, dry contact closure relay panel, and pinhole button for initiation (check-in) to system cloud-based software.

- Top panel: Internal Antenna input terminal

- Dimensions: 17.0”L x 12.0”W x 1.7”D (43.2cm x 30.5cm x 4.32cm)

- Weight: 9 lb. (4.08 kg)

- Operating Range: 32°to 122°F (0° to 50°C)

Specifier Note: For 1 Watt Transmitter, select Internal or External Antenna.

- Internal Antenna: 46.0 in. L (116.8 cm), Weight: 7.75 lb. (3.5kg)

- External Antenna

Cabling: 100 ft. (30.48 m) between transmitter and antenna provided

FCC Part 90 Accepted

IC RSS-119 Accepted

Weight: 9 lb. (4.1kg)

5 Watt Transmitter

Transmitter shall meet the specifications below.

- Operating Frequency Range: 72MHz (Call Sign set to [U.S. FCC] [Canada ISED] license)

- Channels: 49 (set [U.S. FCC] [Canada ISED] license)

- Bluetooth® Wireless Communication Protocol: Bluetooth® Low Energy (BLE) Wireless Technology, version 4.1

- Enclosure Dimensions: 22”W x 17”H x 22”D (55.88 cm x 43.18 cm x 55.88 cm)

- Approx. Weight: 55 lb. (24.9kg)

- AC Power Supply: Input: 120 VAC, 50/60 Hz, 0.6 Amp, Output: 9 VDC, 2.78 Amp, 6 ft. (1.83 m) cord

- Oversized heat sink provides adequate cooling

- Amplifier Output Bandwidth: >20 MHz maximum

- Connector at Antenna; N-male. Maximum 100 ft. (30.4 m) of cabling between transmitter and antenna.

- Front panel: Four LED status indicators (Power, Transmit, Caution, Error) and Bluetooth labeled push-button to pair with the Primex OneVue Device Configurator (ODC) app.

- Rear panel: Network LAN port (RJ-45 Ethernet, 100/10 Mbps, 802.3 Ethernet), GPS In port (MiniDIN 7-Pin), External Antenna connector (coaxial, n-male), Baseboard Monitor port (MiniDIN 9-Pin, for use with 5 or 30 Watt Transmitter, dry contact closure relay panel, and pinhole button for initiation (check-in) to system cloud-based software.

- Operating Range: 32°to 122°F (0° to 50°C)

30 Watt Transmitter

Transmitter shall meet the specifications below.

- Operating Frequency Range: 72MHz (Call Sign set to [U.S. FCC] [Canada ISED] license)

- Channels: 49 (set to [U.S. FCC] [Canada ISED] license)

- Bluetooth® Wireless Communication Protocol: Bluetooth® Low Energy (BLE) Wireless Technology, version 4.1

- Enclosure Dimensions: 22”W x 17”H x 22”D (55.88cm x 43.18cm x 55.88cm)

- Approx. Weight: 55 lb. (24.9kg)

- AC Power Supply: Input: 120 VAC, 50/60 Hz, 0.6 Amp, Output: 9 VDC, 2.78 Amp, 6 ft. (1.83 m) cord

- Oversized heat sink provides adequate cooling

- Amplifier Output Bandwidth: >20 MHz maximum

- Connector at Antenna; N-male. Maximum 100 ft. (30.4 m) of cabling between transmitter and antenna.

- Front panel: Four LED status indicators (Power, Transmit, Caution, Error) and Bluetooth labeled push-button to pair with the Primex OneVue Device Configurator (ODC) app.

- Rear panel: Network LAN port (RJ-45 Ethernet, 100/10 Mbps, 802.3 Ethernet), GPS In port (MiniDIN 7-Pin), External Antenna connector (coaxial, n-male), Baseboard Monitor port (MiniDIN 9-Pin, for use with 5 or 30 Watt Transmitter, dry contact closure relay panel, and pinhole button for initiation (check-in) to system cloud-based software.

- Operating Range: 32° to 122°F (0° to 50°C)

Repeater Transmitter

Specifier Note: Large buildings and multi-building projects may require repeater transmitter to provide proper coverage. Consult Primex for assistance in making this determination. If repeater transmitters are required, include this section. Repeater Transmitter receive broadcasted signal from the main transmitter and broadcast the received signal to the system devices in its vicinity, which are out of range from the main transmitter.

- Operating Frequency Range: 72MHz (Call Sign set to [U.S. FCC] [Canada ISED] license)

- 1 Watt maximum transmission (at transmitter)

- Channels: 49 (set to [U.S. FCC] [Canada ISED] license)

- Bluetooth® Wireless Communication Protocol: Bluetooth® Low Energy (BLE) Wireless Technology, version 4.1

- Dimensions: 17.0”L x 12.0”W x 1.7”D (43.2cm x 30.5cm x 4.32cm)

- Weight: 9 lb. (4.08 kg)

- Power Supply: Input: 120 VAC, 50/60 Hz, 0.6 Amp, Output: 9 VDC, 2.78 Amp, 6 ft. (1.83 m) cord

- Front panel: Four LED status indicators (Power, Transmit, Caution, Error) and Bluetooth labeled push-button to pair with the Primex OneVue Device Configurator (ODC) app.

- Rear panel: Network LAN port (RJ-45 Ethernet, 100/10 Mbps, 802.3 Ethernet), GPS In port (MiniDIN 7-Pin), External Antenna connector (coaxial, n-male) for use with external antenna only, Baseboard Monitor port MiniDIN 9-Pin for use with 5 or 30 Watt Transmitter, dry contact closure relay panel, and pinhole button for initiation (check-in) to system cloud-based software.

- Top panel: Internal Antenna input terminal

- Internal Antenna: 46.0 in. L (116.8 cm), Weight: 7.75 lb. (3.5 kg)

- Operating Range: 32° to 122°F (0° to 50°C)

External antenna specifications

Specifier Note: Section only applies to EXTERNAL Antenna Transmitter models. Delete if a 1 Watt Transmitter with an Internal Antenna Transmitter model is specified.

Transmitter shall include an external antenna that meets the below specifications

- Antenna connects to the transmitter via a 100 ft. (30.5m) 50-ohm coaxial cable.

- 5 and 30 Watt models: External Antenna must be installed by Primex or a certified Primex installer.

- Cabling: Maximum 100 ft. (30.48 m) between transmitter and antenna

- FCC Part 90 Accepted

- IC RSS-119 Accepted

- Weight: 9 lb. (4.1 kg)

- Shall include an Outdoor Ground Plane Antenna that meets the specification below:

Dimensions: 29.4”H x 41.5”W (74.7cm x 105.41cm)

Lightning Protection: Direct Ground

Cabling: 100 ft. (30.48 m) between transmitter and antenna provided

FCC Part 90 Accepted

IC RSS-119 Accepted

Weight: 8.25 lb. (3.75 kg)

GPS Receiver specifications

Specifier Note: If using NTP only for time source input, you may delete this section.

- External Antenna model: GPS roof mounted with 16 ft. (5 m) cable attached. GPS Receiver shall be a complete GPS receiver including antenna in a waterproof case, designed for roof or outdoor mounting. Provide mounting bracket for attachment to roof structure.

- Internal Antenna model: GPS roof mounted, with 10 ft. cable (3 m) attached.

- An GPS extension cable is available from the Manufacturer, 50 ft. (15.25 m), 100 ft. (30.5 m), or 200 ft. (61 m). Use with an external antenna: total GPS cable length cannot exceed 100 ft. (30.5 m).

- GPS Receiver cable must be plenum rated where required by local code.

- GPS connection to main Transmitter requires ferrite bead connector (supplied with transmitter).

Time Source (main Transmitter)

- Transmitter will allow for either NTP time input, or GPS satellite time input with use of a GPS Receiver unit. Unit shall obtain current UTC time from either satellite via GPS, or via NTP through an Ethernet port.

- GPS time source: NTP time source can be used as a backup time source, which requires main Transmitter Ethernet connection.

- Up to three NTP Severs may be specified to ensure continuity of time synchronization.

Digital Display Device (InfoBoard, MiniBoard)

- Receives broadcasted critical communication events from a system transmitter over the 72 MHz radio frequency and serve as a secondary devices to the system transmitter(s).

- Provides up to five digital critical communication events that are invoked by the system main transmitter contact closure control switch (dry contact - normally open or normally closed), or by an integrator system capable of activating contact closure events through an auxiliary jack. One of the five contact closure invokes an all clear notification event. When not in an event mode, devices operate as a digital clock.

- Synchronize its time using Coordinated Universal Time (UTC) derived from a system transmitter. Master time source received from main Transmitter from either a GPS Receiver or a Network Time Protocol (NTP) time source.

- Capable of automatically adjusting for Daylight Saving Time.

- Highly visible LED matrix panel; size of panel and digit characters is dependent on model supplied; viewable from up to 150 ft. (45.7 m).

- Power outage memory backup and maintain correct time up to a minimum of 1 hour without power.

- Operate with a free running accuracy of .45 seconds per day, and will continue to operate in the absence of NTP time source.

- Powered by AC (120 VAC/50-60 cycle) with a 10 ft. (3.0 m) power cord with a two-prong plug. Power plug may be removed and cord cut to length for hardwired (pigtail) installation. Pigtail installation requires a 120V~ power line in a junction box installed by a licensed electrician.

- Fully portable, capable of being relocated at any time.

SUPPLY MODELS

Large InfoBoard - Surface Mount (Part no. NT2008A300)

- Wireless Radio Technology: 72 MHz

- Power over Ethernet: IEEE 802.3af standard and compatible with 802.3at standard

- Bluetooth® Wireless Communication Protocol: Bluetooth® Low Energy (BLE) Wireless Technology, version 4.1

- AC power: 120 VAC (100-240)/ 50–60 cycle, 10 ft. (3.0 m) cord with two-prong plug, UL/cUL listed

- Weight: 4.3 lb. (2.0kg)

- Dimensions: 8.25” (21.0cm) H x 20.875” (53.0cm) W x 2.625” (6.7cm) D

- Junction box: UL listed (UL 50E 1st Ed; listing number E469550)

- 100 dB internal speaker

- Ethernet port: 10/100M RJ45

- RJ11 port: Timer Control Switch connection for use with Code Blue Timer and Elapsed Timer function

Medium InfoBoard - Surface Mount (Part No. NT2008A200)

- Wireless Radio Technology: 72 MHz

- Power over Ethernet: IEEE 802.3af standard and compatible with 802.3at standard

- Bluetooth® Wireless Communication Protocol: Bluetooth® Low Energy (BLE) Wireless Technology, version 4.1

- AC power: 120 VAC (100-240)/ 50–60 cycle, 10 ft. (3.0 m) cord with two-prong plug, UL/cUL listed

- Weight: 3.5 lb. (1.6 kg)

- Dimensions: 8.25” (21.0 cm) H x 14.576” (37.0 cm) W x 2.625” (6.7 cm) D

- Enclosure: ABS plastic. Junction box: UL listed (UL 50E 1st Ed; listing number E469550)

- 100 dB internal speaker

- Ethernet port: 10/100M RJ45

- RJ11 port. Timer Control Switch connection for use with Code Blue Timer and Elapsed Timer function

MiniBoard (Part No. NT2008A100)

- Wireless Radio Technology: 72 MHz

- Power over Ethernet: IEEE 802.3af standard and compatible with 802.3at standard

- Bluetooth® Wireless Communication Protocol: Bluetooth® Low Energy (BLE) Wireless Technology, version 4.1

- AC power: 120 VAC (100-240)/ 50–60 cycle, 10 ft. (3.0 m) cord with two-prong plug, UL/cUL listed

- Weight: 1.85 lb. (0.8kg)

- Dimensions: 9.625” (24.4cm) H x 9.25” (23.5cm) W x 2.25” (5.7cm) D

- Junction box: UL listed (UL 50E 1st Ed; listing number E469550)

- Ethernet port: 10/100M RJ45

- RJ11 port: Timer Control Switch connection for use with Code Blue Timer and Elapsed Timer function

Accessories

- MiniBoard Desktop Stand (Part No. NT1XSTND)

- Medium InfoBoard - Dual Mount Kit (Ceiling or Wall) (Part No. NT2XBRK)

- Large InfoBoard - Dual Mount Kit (Ceiling Only) (Part No. NT3XBRK)

- Critical Notification Panel (Part No. NTPANEL). RJ50 10-pin conductor cable; maximum cable length 1000 ft. (304.8 m)

- Elapsed Timer/Code Blue Timer Kit (RJ-11 cable, Code Blue timer connector, Timer Control Switch). For Code Blue Timer and Elapsed Timer operation.

- Timer Control Switch (Part No. Q13800). For Code Blue Timer and Elapsed Timer operation.

PART 3 EXECUTION

3.1 EXAMINATION

- Examine conditions with the Installer present for compliance with requirements and other conditions affecting the performance of the system and the system devices.

- Do not proceed until unsatisfactory conditions have been corrected.

- Verify that construction is complete in spaces to receive equipment and that rooms are clean and dry.

- Verify that 120 VAC electrical outlet is located within 5 ft. (1.5 m) of device and the outlet is operational and properly grounded.

- Timer Switch Control: Verify single gang electrical box for switch control is mounted and within 15 ft. (4.5 m) of digital display device. Verify pathway for connecting cable is available and compliant to local building codes.

- PoE devices: Verify that an active PoE port is located within close proximity to device.

3.2 INSTALLATION

Specifier Note: To assure optimum performance of the system, a site survey is recommended to be performed by Primex or a Certified Primex installation company. To assure optimum performance of the Time Synchronization System, transmitter(s) location (s) must be specified in the construction documents. Contact Primex Technical Support.

- General: Install system devices in accordance with applicable codes.

- Install system devices in accordance with Manufacturer written instructions. Refer to Manufacturer System Setup Illustrations for reference.

- Provide all system equipment necessary for a complete and operable system.

- Comply with requirements of Division 27 Sections "Common Work Results for Communications" and "Communications Horizontal Cabling."

- Cables: Install cables in raceways and cable trays except within consoles, cabinets, and desks [and except in accessible ceiling spaces and framed partitions where exposed wiring is allowed by Owner]. Install plenum cable where required. Conceal cable installation where possible.

Specifier Note: Valid for transmitter with GPS input. The GPS unit can be mounted on the roof, on a pole, or at a window. In each case, the GPS unit must have a clear view of the sky. If the GPS unit is mounted on the roof, it must be located on a suitable bracket, well above the level of standing or incidental water. If the GPS unit is mounted at a window, it must be located away from low-E glass. If transmitter to use NTP as time source, delete following work instruction with this note.

GPS Unit (INTERNAL Antenna Transmitter Model only):

- Install GPS unit on roof in location indicated, in clear view of the sky.

- Install unit in location free from standing water and above accumulations of leaves or debris.

- Seal cable connection to GPS with cable connection sealant.

- Any added cable lengths must be protected from outside elements.

GPS Unit (EXTERNAL Antenna Transmitter Model only):

- Locate transmitter in a penthouse, electrical closet or telecommunications room in a central location in the building.

- Clearance around all side of the transmitter to comply with local building codes.

Specifier Note: Select procedure appropriate to the master time source from either of the following:

If GPS Unit will be used as master time source:

- Attach GPS receiver to transmitter using cable.

If NTP will be used as master time source:

Specifier Note: If NTP is the master time source, the network drop used to connect the transmitter must have connectivity to the NTP server, which can be verified by the owner's Information Technology department manager. The default NTP address is time.nist.gov. If the network has a different NTP IP address, it may be programmed into the transmitter by the installer to allow connection to the proper network time.

- Connect CAT5/CAT5e/CAT6 EIA/TIA standard Ethernet cable from transmitter LAN port to available network drop.

Transmitter (EXTERNAL Antenna only)

- Install transmitter and all components per Manufacturer provided instructions.

- Transmitter is connected to external antenna via a 50 ohm coaxial cable. Typical length 100 ft. (30.5 m)

- Cable routing should comply with ANSI EIA/TIA-569 and local building codes.

- If cable is routed through conduit, the conduit should be a minimum of 2 inch (50.8 mm) diameter.

- Transmitter enclosure must be bonded to an earth ground per ANSI EIA/TIA 607, NEC Article 250, and local building codes.

- Antenna should be mounted to a mast on the roof of the building connecting to the transmitter via a 50-ohm coaxial cable.

- Consult manufacturer instruction manual for specific clearances and mounting instructions.

- Antenna must be bonded to an earth ground per ANSI EIA/TIA 607, NEC Article 250, and local building codes.

- Connect external antenna to transmitter.

- Main transmitter: Connect contact closure inputs and time source.

- Connect power supply to the transmitter.

- Plug power supply into electrical outlet.

- Configure transmitter with Manufacturer supplied mobile app.

Transmitter (1 Watt with Internal Antenna and Repeater Transmitter)

- Install transmitter and all components per Manufacturer provided instructions.

- Locate transmitter where indicated on drawings; a minimum of 4 ft. (1.2 m) above the floor, away from large metal objects such as filing cabinets, lockers or metal framed walls.

- Transmitter(s) will be placed at locations indicated within specifications and drawings.

- Connect antenna to transmitter top panel, using care not to strip threads.

- Main transmitter: Connect contact closure inputs and time source.

- Connect power supply to the transmitter.

- Plug power supply into electrical outlet.

- Configure transmitter with Manufacturer supplied mobile app.

Digital Display Devices (InfoBoards/MiniBoards)

- System transmitter(s) are to be fully operational before installing or operating devices.

- Cable routing must comply with ANSI EIA/TIA- 569-A and local building codes.

- Furnish all equipment necessary for a complete and operational system.

- Install each device per its model mounting specifications per Manufacturer instructions and mounting instructions at the indicated location.

- Perform the following operations with each device:

  - Configure transmitter with Manufacturer supplied mobile app.

  - Observe device until valid signals are received and device adjusts itself to correct time.

- For code blue or elapsed timer use, connect device to Manufacturer timer control switch unit with provided cable or approved extension cable.

3.3 FIELD INSPECTION

- Inspection: Make observations to verify that system devices and components are properly labeled.

- Prior to final acceptance, inspect each system device and component, adjust as required, and replace parts which are found defective.

- At completion of system device installation and prior to final acceptance, turn on the equipment; ensure that all equipment is operating properly, and that the system and all system devices and components are functioning.

3.4 MANUFACTURER SERVICES

- System software and device manuals shall be assessable through Manufacturer online knowledge base

- Provide Manufacturer system commissioning in accordance with Manufacturer written recommendations. Perform operational testing to verify compliance with requirements. Adjust as required.

- Manufacturer to provide a specified level of system commissioning services.

Specifier Note: Only include one level of commissioning. Contact Primex for additional information.

- Phone commissioning: system deployment training, including system set up, validation of device configuration, and system functionality by way of a remote web conference.

- On-site commissioning: system deployment training, including system set up, validation of device configuration, system functionality, verification of device network connections, and device install training.

- Installation and full on-site commissioning: system training, software configuration, validation of device configuration, training on system functionality, verification of network use, device install training, and device installation.

3.5 CLEANING

- Prior to final acceptance, clean exposed surfaces of devices, using cleaning methods recommended by Manufacturer.

- Remove temporary labels from devices faces. Do not remove labels from the back of devices.

3.6 DEMONSTRATION

- Provide training to OWNER'S representative on setting, adjusting and configuring device and routine maintenance.

- Provide training to OWNER'S representative on using the system software or mobile app, configuring system device settings, adjusting system devices, and routine maintenance.

3.7 PROTECTION

- Protect finished installation until final acceptance of the project.

3.8 TESTING

- All devices must be tested at their operational location under normal operational conditions to ensure reception of system signal.